## 3.4 Critical velocity
Cv-Critical velocity and HRR-Heat release rate(2005-Lee)
Scale | Length (m) | Fuel
1:20 | 10.4 | ethanol pool fire
Width (m) | 0.6 | 0.5 | 0.4 | 0.333 | 0.3
Height (m) | 0.3 | 0.333 | 0.4 | 0.5 | 0.6
HRR (kW) | 2.47 | 3.84 | 5.63 | 8.27 | 9.96 | 12.3
AS is the aspect ratio
AS = 0.5 | HRR/kW | 2.47 | 3.84 | 5.63 | 8.27 | 9.96 | 12.3
| Cv/(m/s) | 0.4198 | 0.4613 | 0.5074 | 0.5522 | 0.5716 | 0.5819
AS = 0.667 | HRR | 2.47 | 3.84 | 5.63 | 8.27 | 9.96 | 12.3
| Cv | 0.4233 | 0.4682 | 0.5154 | 0.5603 | 0.5878 | 0.6085
AS = 1.0 | HRR | 2.47 | 3.84 | 5.63 | 8.27 | 9.96 | 12.3
| Cv | 0.429 | 0.4775 | 0.5166 | 0.5718 | 0.5972 | 0.6189
AS = 1.5 | HRR | 2.47 | 3.84 | 5.63 | 8.27 | 9.96 | 12.3
| Cv | 0.4499 | 0.5041 | 0.5386 | 0.5951 | 0.6179 | 0.6513
AS = 2.0 | HRR | 2.47 | 3.84 | 5.63 | 8.27 | 9.96 | 12.3
| Cv | 0.4719 | 0.5226 | 0.5594 | 0.6333 | 0.6597 | 0.6918
V-Ventilation velocity and HRR-Heat release rate by different backing up distance(1995-Oka)
Tunnel information
Scale | Length (m) | Width (m) | Height (m) | Fuel
reduced scale | 15 | 0.274 | 0.244 | Propane gas
HRR (kW) | 0.4318 | 0.7174 | 1.4485 | 2.906 | 7.2684 | 14.3807 | 29.0107
Burner Size | 10 cm x 10 cm | 4 cm x 14 cm | 4 mm x 236 mm | 7 cm × 8 cm
Burner location | Centre | Beside wall | 130 mm height
backing up distance
1 tunnel height | HRR/kW | 0.4318 | 0.7174 | 1.4485 | 2.906 | 7.2684 | 14.3807 | 29.0107
| V/(m/s) | 0.2566 | 0.3032 | 0.3785 | 0.4607 | 0.5167 | 0.5192 | 0.514
3 tunnel height | HRR | 0.4318 | 0.7174 | 1.4485 | 2.906 | 7.2684 | 14.3807 | 29.0107
| V | 0.2091 | 0.2624 | 0.3226 | 0.3988 | 0.4539 | 0.4584 | 0.4493
5 tunnel height | HRR | 0.4318 | 0.7174 | 1.4485 | 2.906 | 7.2684 | 14.3807 | 29.0107
| Cv | 0.1679 | 0.2214 | 0.282 | 0.3383 | 0.4027 | 0.4149 | 0.4087
10 tunnel height | HRR | 0.4318 | 0.7174 | 1.4485 | 2.906 | 7.2684 | 14.3807
| V | 0.1202 | 0.1726 | 0.2154 | 0.2898 | 0.3216 | 0.3348
V*-Dimensionless critical velocity and Q*-Dimensionless heat release rate (1995-Oka)
burner 1 zero back-up | Q* | 0.0133 | 0.0221 | 0.0438 | 0.0873 | 0.2185 | 0.4386 | 0.8807
| V* | 0.1792 | 0.2106 | 0.2628 | 0.3197 | 0.3523 | 0.3536 | 0.3472
V*-Dimensionless critical velocity and Q*-Dimensionless heat release rate by different burner(1995-Oka)
burner 1 | Q* | 0.0133 | 0.022 | 0.044 | 0.088 | 0.22 | 0.44 | 0.88
| V* | 0.1792 | 0.2106 | 0.2628 | 0.3197 | 0.3523 | 0.3536 | 0.3472
burner 4 | Q* | 0.022 | 0.044 | 0.088 | 0.22 | 0.44 | 0.88
| V* | 0.1504 | 0.2063 | 0.2561 | 0.3078 | 0.3143 | 0.3023
burner 7 | Q* | 0.022 | 0.044 | 0.088 | 0.22 | 0.44 | 0.88
| V* | 0.2574 | 0.3043 | 0.3559 | 0.3787 | 0.3877 | 0.3894
burner 8 | Q* | 0.022 | 0.044 | 0.088 | 0.22 | 0.44
| V* | 0.2099 | 0.2586 | 0.2988 | 0.3276 | 0.3245
burner 9 | Q* | 0.022 | 0.044 | 0.088 | 0.22 | 0.44
| V* | 0.139 | 0.1672 | 0.1954 | 0.217 | 0.2236
V*max - Normalized dimensionless critical velocity and Q*-Dimensionless heat release rate by different burner(1995-Oka)
burner 1 | Q* | 0.0133 | 0.022 | 0.0439 | 0.0889 | 0.222 | 0.4455
| V*max | 0.5067 | 0.5931 | 0.7418 | 0.9037 | 0.9949 | 0.9985
burner 4 | Q* | 0.022 | 0.0439 | 0.0883 | 0.2219 | 0.8939
| V*max | 0.5931 | 0.7418 | 0.9001 | 0.9792 | 0.9889
burner 7 | Q* | 0.0219 | 0.0441 | 0.0887 | 0.8936 | 0.222
| V*max | 0.4828 | 0.6602 | 0.8174 | 0.9639 | 0.9805
burner 8 | Q* | 0.0218 | 0.0439 | 0.9109
| V*max | 0.6638 | 0.7429 | 0.9998
burner 9 | Q* | 0.0221 | 0.0439 | 0.44 | 0.0889 | 0.2207
| V*max | 0.6434 | 0.7909 | 1.0021 | 0.9156 | 1.0044
V* - Dimensionless critical velocity and Q*-Dimensionless heat release rate -effect of burner shape(1995-Oka)
burner 2 | Q* | 0.0131 | 0.0218 | 0.0436 | 0.0867 | 0.2168 | 0.4328 | 0.8638
| V* | 0.1486 | 0.1848 | 0.222 | 0.282 | 0.3171 | 0.3201 | 0.3144
burner 3 | Q* | 0.0131 | 0.0215 | 0.0436 | 0.0868 | 0.2144 | 0.4334 | 0.8652
| V* | 0.1638 | 0.2009 | 0.2464 | 0.3174 | 0.3568 | 0.3653 | 0.3663
burner 4 | Q* | 0.0217 | 0.0436 | 0.0866 | 0.214 | 0.4327 | 0.8634
| V* | 0.1516 | 0.2086 | 0.2559 | 0.3084 | 0.3157 | 0.3014
V* - Dimensionless critical velocity and Q*-Dimensionless heat release rate -effect of burner location(1995-Oka)
burner 5 | Q* | 0.0221 | 0.0441 | 0.445
| V* | 0.1967 | 0.2481 | 0.3719
burner 6 | Q* | 0.0221 | 0.0441 | 0.089 | 0.2219 | 0.4422
| V* | 0.1854 | 0.2372 | 0.3033 | 0.3484 | 0.3618
burner 7 | Q* | 0.0221 | 0.0444 | 0.0885 | 0.222 | 0.4424 | 0.8869
| V* | 0.2596 | 0.3045 | 0.3571 | 0.38 | 0.3879 | 0.3905
V* - Dimensionless critical velocity and Q*-Dimensionless heat release rate -effect of blockage(1995-Oka)
burner 7 | Q* | 0.022 | 0.0442 | 0.0894 | 0.2227 | 0.444 | 0.8902
| V* | 0.2594 | 0.305 | 0.355 | 0.38 | 0.3889 | 0.3885
burner 8 | Q* | 0.0221 | 0.0439 | 0.0881 | 0.2225 | 0.4434
| V* | 0.2128 | 0.2591 | 0.2995 | 0.3284 | 0.3269
burner 9 | Q* | 0.0222 | 0.044 | 0.0884 | 0.2218 | 0.4447
| V* | 0.1418 | 0.1679 | 0.1961 | 0.2181 | 0.224
V - Critical velocity and Q - Heat release rate (2000-Wu)
Tunnel information
Scale | Length (m) | Height (m) | Fuel
1:10 | 15 | 0.25 | Propane gas
Width (m) | 0.136 | 0.25 | 0.5 | 1
HRR (kW) | 1.5 | 3 | 7.5 | 10.5 | 12 | 15 | 22.5 | 30
Burner | 106 mm diameter porous bed burner
tunnel E (arch) | 0.244 m Height | cross-sectional 0.0569 m2
Tunnel A | Q | 1.5 | 3 | 7.5 | 10.5 | 12 | 15 | 22.5 | 30
| V | 0.43 | 0.46 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48
Tunnel B | Q | 1.5 | 3 | 7.5 | 10.5 | 12 | 15 | 22.5 | 30
| V | 0.39 | 0.48 | 0.56 | 0.59 | 0.6 | 0.6 | 0.6 | 0.6
Tunnel C | Q | 1.5 | 3 | 7.5 | 10.5 | 12 | 15 | 22.5 | 30
| V | 0.37 | 0.45 | 0.54 | 0.57 | 0.59 | 0.6 | 0.62 | 0.65
Tunnel D | Q | 1.5 | 3 | 7.5 | 10.5 | 12 | 15 | 22.5 | *
| V | 0.34 | 0.4 | 0.5 | 0.54 | 0.56 | 0.59 | 0.65 | *
Tunnel E | Q | 1.5 | 3 | 7.5 | 10.5 | 12 | 15 | 22.5 | 30
| V | 0.44 | 0.54 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Buxton | Q | 204 | 606 | 1040 | 1290 | 570 | 1230 | 204
| V | 0.908 | 1.438 | 1.363 | 1.4 | 1.037 | 1.387 | 0.757
Memorial | Q | 10000 | 100000
| V | 2.5 | 3
EUREKA | Q | 100000
| V | 2.8
V'' - Dimensionless critical velocity and Q''-Dimensionless heat release rate - based on hydraulic tunnel height(2000 Wu)
Tunnel A | Q'' | 0.108 | 0.216 | 0.539 | 0.754 | 0.862 | 1.078 | 1.616 | 2.155
| V'' | 0.333 | 0.356 | 0.372 | 0.372 | 0.372 | 0.372 | 0.372 | 0.372
Tunnel B | Q'' | 0.041 | 0.082 | 0.205 | 0.288 | 0.329 | 0.411 | 0.616 | 0.822
| V'' | 0.248 | 0.309 | 0.354 | 0.379 | 0.382 | 0.382 | 0.382 | 0.382
Tunnel C | Q'' | 0.021 | 0.041 | 0.103 | 0.144 | 0.164 | 0.205 | 0.308 | 0.41
| V'' | 0.203 | 0.251 | 0.298 | 0.319 | 0.325 | 0.332 | 0.344 | 0.359
Tunnel D | Q'' | 0.01 | 0.02 | 0.05 | 0.07 | 0.08 | 0.1 | 0.15 | *
| V'' | 0.162 | 0.192 | 0.241 | 0.259 | 0.27 | 0.284 | 0.313 | *
Tunnel E | Q'' | 0.046 | 0.093 | 0.232 | 0.325 | 0.372 | 0.465 | 0.67 | 0.929
| V'' | 0.288 | 0.353 | 0.393 | 0.393 | 0.393 | 0.393 | 0.393 | 0.393
Buxton | Q'' | 0.019 | 0.056 | 0.096 | 0.119 | 0.052 | 0.113 | 0.019
| V'' | 0.188 | 0.298 | 0.282 | 0.29 | 0.215 | 0.287 | 0.157
Memorial | Q'' | 0.051 | 0.513
| V'' | 0.287 | 0.344
EUREKA | Q'' | 1.067
| V'' | 0.375
V* - Dimensionless critical velocity and Q* - Dimensionless heat release rate - based on tunnel height(2000 Wu)
calculated from V-Q data
V - Critical velocity and Q - Heat release rate (2010-Li)
Tunnel information
Scale | Fuel | Length (m)
small scale | Propane gas | 12
Tunnel A | 0.25 m height | 0.25 m width | 100 mm diameter porous bed burner
Tunnel B (arch) | 0.393 height |  | 150 mm diameter burner
Tunnel A | Q | 0.7 | 1.6 | 1.8 | 2 | 3.2 | 4.8 | 6.7 | 9.3 | 12.9 | 16.7
| V | 0.33 | 0.46 | 0.49 | 0.5 | 0.57 | 0.63 | 0.66 | 0.67 | 0.67 | 0.67
Tunnel B | Q | 2 | 2.2 | 3.5 | 4.6 | 5.9 | 7.2 | 8.5 | 9.4 | 11.1 | 12.4 | 14.4 | 14.8 | 16.9 | 18.4
| V | 0.43 | 0.45 | 0.53 | 0.58 | 0.63 | 0.67 | 0.7 | 0.72 | 0.76 | 0.77 | 0.8 | 0.78 | 0.82 | 0.82
Tunnel B (with vehicle) | Q | 1.7 | 2.9 | 4 | 5.7 | 6.9 | 9.2 | 10.9 | 13.1 | 15.2 | 15.6 | 16.8 | 18.8 | 19.7 | 23.2
| V | 0.3 | 0.38 | 0.42 | 0.48 | 0.51 | 0.57 | 0.59 | 0.6 | 0.62 | 0.61 | 0.64 | 0.65 | 0.64 | 0.65
V - Ventilation velocity and - Tunnel slope (1997 Atkinson)
Tunnel information
Scale | Fuel | height
small scale | Propane gas | 0.244
cross-section | BS 227 colliery arch
Burner | 100 mm diameter porous bed burner
1 tunnel height | Q* = 0.44 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.6692 | 0.6923 | 0.697 | 0.7029 | 0.741 | 0.7572
| Q* = 0.22 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.6564 | 0.6762 | 0.6832 | 0.6914 | 0.7156 | 0.7388
| Q* = 0.088 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.5516 | 0.5403 | 0.613 | 0.5992 | 0.6097 | 0.6259
3 tunnel height | Q* = 0.44 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.5929 | 0.6088 | 0.6259 | 0.6301 | 0.6625 | 0.662
| Q* = 0.22 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.5764 | 0.5735 | 0.6212 | 0.6231 | 0.6484 | 0.6491
| Q* = 0.088 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.479 | 0.4961 | 0.5213 | 0.5268 | 0.5356 | 0.5423
5 tunnel height | Q* = 0.44 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.5102 | 0.5524 | 0.5689 | 0.5713 | 0.5918 | 0.6014
| Q* = 0.22 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.4898 | 0.5168 | 0.5455 | 0.5585 | 0.5574 | 0.5786
| Q* = 0.088 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.4319 | 0.4536 | 0.4794 | 0.4689 | 0.4755 | 0.4774
10 tunnel height | Q* = 0.44 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.3885 | 0.4635 | 0.4642 | 0.4748 | 0.4863 | 0.4653
| Q* = 0.22 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.3791 | 0.4386 | 0.4501 | 0.4466 | 0.4485 | 0.4487
| Q* = 0.088 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
|  | ventilation velocity | 0.3143 | 0.3727 | 0.3735 | 0.3689 | 0.3684 | 0.3734
Q* = 0.44 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
| critical velocity | 1.0003 | 1.03 | 1.0404 | 1.0493 | 1.1018 | 1.1481
Q* = 0.22 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
| critical velocity | 1.001 | 1.0141 | 1.0307 | 1.0451 | 1.0728 | 1.135
Q* = 0.088 | tunnel slope | 0 | 2 | 4 | 6 | 8 | 10
| critical velocity | 1.001 | 0.9698 | 1.1199 | 1.0742 | 1.1171 | 1.162
V - Critical velocity and - nozzle diameter (2005 Vauquelin)
Tunnel information
Scale | small scale
Length (m) | 10
height (m) | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4
width (m) | 0.13 | 0.225 | 0.3 | 0.4 | 0.5 | 0.6
slope | from -20% to +20%
HRR (kW) | 0.1-10
D/H | 0.1081 | 0.1405 | 0.1602 | 0.1973 | 0.2576 | 0.3332 | 0.4933 | 0.6642
Uc* | 0.2809 | 0.2732 | 0.2624 | 0.2388 | 0.2407 | 0.2496 | 0.2591 | 0.2765
V* - Dimensionless critical velocity and -Q* Dimensionless heat release rate (2005 Vauquelin)
Q* | 0.0016169 | 0.003079 | 0.0047255 | 0.0079993 | 0.0162 | 0.0322 | 0.0821 | 0.1615
V* | 0.1654 | 0.1892 | 0.2196 | 0.2384 | 0.2753 | 0.31 | 0.3473 | 0.3635
Uc - Critical velocity and - S channel slope (2005 Vauquelin)
S (%) | -15.4685 | -8.6846 | -3.4604 | 0.0346 | 3.4949 | 8.8245 | 15.4341
Uc (m/s) | 1.1232 | 1.0974 | 1.03 | 0.9999 | 0.9674 | 0.9353 | 0.8814
Uc - Critical velocity and - H channel height (2005 Vauquelin)
Source n 4 | H (cm) | 10.0021 | 15 | 20 | 25 | 30 | 35 | 40
| Uc (m/s) | 0.3201 | 0.3307 | 0.3511 | 0.3692 | 0.3801 | 0.3798 | 0.3889
Source n 6 | H (cm) | 10.0021 | 15 | 20 | 25 | 30 | 35 | 40
| Uc (m/s) | 0.3397 | 0.4097 | 0.441 | 0.4897 | 0.4791 | 0.4788 | 0.4697
Uc - Critical velocity and - W channel width (2005 Vauquelin)
Source n 4 | W (cm) | 13 | 22.5 | 30 | 40 | 50 | 60
| Uc (m/s) | 0.421 | 0.3998 | 0.3893 | 0.3795 | 0.369 | 0.3484
Source n 5 | W (cm) | 13 | 22.5 | 30 | 40 | 50 | 60
| Uc (m/s) | 0.3689 | 0.4294 | 0.4402 | 0.4402 | 0.4295 | 0.4089
Source n 6 | W (cm) | 13 | 22.5 | 30 | 40 | 50 | 60
| Uc (m/s) | 0.3791 | 0.4802 | 0.5095 | 0.4997 | 0.4887 | 0.4485
Uc - Critical velocity and - W tunnel width - Based on Thermal model (2006 Vauquelin)
Exp#1 - 1.5kW | W (cm) | 13.5 | 25 | 50 | 100 |  |  | Tunnel information
| Uc (m/s) | 0.4301 | 0.3896 | 0.3704 | 0.3405 |  |  | Scale | 1:20 |  | Fuel | Propane gas
Exp#1 - 3.0kW | W (cm) | 13.5 | 25 | 50 | 100 |  |  | Length (m) | 18 |  | fire source | 106 mm diameter porous bed burner
| Uc (m/s) | 0.4599 | 0.4804 | 0.4501 | 0.4001 |  |  | height (m) | 0.25
Exp#1 - 7.5kW | W (cm) | 13.5 | 25 | 50 | 100 |  |  | width (m) | 0.136 | 0.25 | 0.5 | 1
| Uc (m/s) | 0.4804 | 0.5614 | 0.5404 | 0.5017 |  |  | construction material: 6.25 mm thickness PMMA + 1.25 mm thick 18 SWG stainless steel
Exp#1 - 15kW | W (cm) | 13.5 | 25 | 50 | 100 |  |  | HRR (kW) | 1.4-28
| Uc (m/s) | 10.0021: 0.4799; 15: 0.6; 20: 0.6; 25: 0.5901
Uc - Critical velocity and - W tunnel width - Based on Densimetrical model (2006 Vauquelin)
Exp#2 - 0.56kW | W (cm) | 13 | 22.5 | 30 | 40 | 50 | 60
| Uc (m/s) | 0.4207 | 0.4001 | 0.3889 | 0.3805 | 0.369 | 0.3491
Exp#2 - 1.12kW | W (cm) | 13 | 22.5 | 30 | 40 | 50 | 60
| Uc (m/s) | 0.369 | 0.4294 | 0.4405 | 0.4405 | 0.4294 | 0.4095
Exp#2 - 2.24kW | W (cm) | 13 | 22.5 | 30 | 40 | 50 | 60
| Uc (m/s) | 0.3808 | 0.4818 | 0.5108 | 0.5017 | 0.4905 | 0.4506
V - Critical velocity and Q - Heat release rate (2008-Roh)
Tunnel information
Scale | 1:20 | 10.0021: Fuel; 15: n-heptane (C7H16)
Length (m) | 10
height (m) | 0.4
width (m) | 0.4
pool fire size (cm) | 4.5 | 10.0021: 5.5; 15: 6.5; 20: 8.5
walls material: 0.01 m thick transparent acryl
HRR (kW) | 2.23-15.56
critical velocity
Reduced-scale value | 4.5 | QM (kW) | 2.23 | 4.43 | 4.97 | 5.94
|  | VM (m/s) | 0 | 0.44 | 0.87 | 1.33
| 5.5 | QM (kW) | 3.71 | 5.93 | 6.31 | 7.42
|  | VM (m/s) | 0 | 0.46 | 0.92 | 1.38
| 6.5 | QM (kW) | 5.8 | 7.35 | 8.3 | 9.57
|  | VM (m/s) | 0 | 0.48 | 0.96 | 1.44
| 8.5 | QM (kW) | 10.95 | 11.7 | 12.9 | 15.6
|  | VM (m/s) | 0 | 0.56 | 1.12 | 1.68
Full-scale value | 4.5 | QM (kW) | 3.9 | 7.92 | 8.9 | 10.6
|  | VM (m/s) | 0 | 1.97 | 3.89 | 5.95
| 5.5 | QM (kW) | 6.6 | 10.6 | 11.3 | 13.3
|  | VM (m/s) | 0 | 2.06 | 4.1 | 6.17
| 6.5 | QM (kW) | 10.4 | 13.1 | 14.8 | 17.1
|  | VM (m/s) | 0 | 2.15 | 4.3 | 6.44
| 8.5 | QM (kW) | 19.6 | 20.9 | 23.9 | 27.9
|  | VM (m/s) | 0 | 2.5 | 5.01 | 7.51
Ucr- Critical velocity and D - distance from the tunnel exit (2011-Tsai)
6.3*6.3 cm fire | Ucr (m/s) | 10.0021: 0.5; 15: 1; 20: 1.5; 25: 2
| D (m) | 10.0021: 0.2594; 15: 0.3394; 20: 0.3878; 25: 0.4687
9*9 cm fire | Ucr (m/s) | 10.0021: 0.5; 15: 1; 20: 1.5; 25: 2
| D (m) | 10.0021: 0.3324; 15: 0.4626; 20: 0.5039; 25: 0.6428
Ucr- Critical velocity with 6.3*6.3 cm2 fire and vehicles in two arrays (2012-Lee)
No. | Fire size | Tunnel height | Vehicle size | Fire position | Separation between vehicle and fire | HRR (kW) | ucr (m/s)
A-1 | 6.3*6.3 | 60cm | No vehicle | Central line | – | 4.05 | 0.37
A-2 |  |  | Small vehicle | Central line | 0.05 m | 4.31 | 0.38
A-3 |  | 25: 0.1 m; 30: 4.29; 35: 0.37
A-4 |  | 25: 0.15 m; 30: 4.3; 35: 0.37
A-5 |  | 20: Before vehicle; 25: 0.05 m; 30: 4.58; 35: 0.37
A-6 |  | 25: 0.1 m; 30: 4.44; 35: 0.36
A-7 |  | 25: 0.15 m; 30: 4.49; 35: 0.36
A-8 |  |  | Medium vehicle | Central line | 0.05 m | 4.38 | 0.33
A-9 |  | 25: 0.1 m; 30: 4.09; 35: 0.32
A-10 |  | 25: 0.15 m; 30: 4.29; 35: 0.34
A-11 |  | 20: Before vehicle; 25: 0.05 m; 30: 4.86; 35: 0.42
A-12 |  | 25: 0.1 m; 30: 4.77; 35: 0.42
A-13 |  | 25: 0.15 m; 30: 4.7; 35: 0.4
A-14 |  |  | Large vehicle | Central line | 0.05 m | 4.46 | 0.32
A-15 |  | 20: Before vehicle; 25: 0.05 m; 30: 5.81; 35: 0.48
A-16 |  | 40cm | No vehicle | Central line | – | 4.25 | 0.58
A-17 |  |  | Medium vehicle | Central line | 0.05 m | 4.51 | 0.48
A-18 |  | 20: Before vehicle; 30: 5.03; 35: 0.5
A-19 |  |  | Large vehicle | Central line | 0.05 m | 4.7 | 0.43
A-20 |  | 20: Before vehicle; 25: 0.05 m; 30: 8.26; 35: 0.62
Ucr- Critical velocity with 9.0*9.0 cm2 fire and vehicles in two arrays (2012-Lee)
No. | Fire size | Tunnel height | Vehicle size | Fire position | Separation between vehicle and fire | HRR (kW) | ucr (m/s)
B-1 | 9.0*9.0 | 60cm | No vehicle | Central line | – | 9.51 | 0.5
B-2 |  |  | Small vehicle | Central line | 0.05 m | 8.79 | 0.5
B-3 |  | 25: 0.1 m; 30: 8.54; 35: 0.49
B-4 |  | 25: 0.15 m; 30: 8.77; 35: 0.5
B-5 |  | 20: Before vehicle; 25: 0.05 m; 30: 8.95; 35: 0.49
B-6 |  | 25: 0.1 m; 30: 8.9; 35: 0.5
B-7 |  | 25: 0.15 m; 30: 8.93; 35: 0.49
B-8 |  |  | Medium vehicle | Central line | 0.05 m | 8.93 | 0.43
B-9 |  | 25: 0.1 m; 30: 8.99; 35: 0.45
B-10 |  | 25: 0.15 m; 30: 8.91; 35: 0.46
B-11 |  | 20: Before vehicle; 25: 0.05 m; 30: 10.75; 35: 0.54
B-12 |  | 25: 0.1 m; 30: 10.7; 35: 0.54
B-13 |  | 25: 0.15 m; 30: 10.72; 35: 0.54
B-14 |  |  | Large vehicle | Central line | 0.05 m | 8.79 | 0.42
B-15 |  | 20: Before vehicle; 25: 0.05 m; 30: 12.13; 35: 0.55
B-16 |  | 40cm | No vehicle | Central line | – | 9.5 | 0.7
B-17 |  |  | Medium vehicle | Central line | 0.05 m | 9.85 | 0.63
B-18 |  | 20: Before vehicle; 30: 15.31; 35: 0.75
B-19 |  |  | Large vehicle | Central line | 0.05 m | 10.42 | 0.54
B-20 |  | 20: Before vehicle; 25: 0.05 m; 30: 16.01; 35: 0.85
Ucr- Critical velocity with vehicles in two arrays (2012-Lee)
No. | Fire size | Tunnel height | Vehicle size | Fire position | Separation between vehicle and fire | HRR (kW) | ucr (m/s)
C-1 | 6.3*6.3 cm2 | 60cm | No vehicle | Central line | - | 3.84 | 0.37
C-2 |  |  | Small vehicle | Central line + Before vehicle | 0.05 m | 3.61 | 0.4
C-3 |  | 25: 0.1 m; 30: 3.44; 35: 0.39
C-4 |  | 25: 0.15 m; 30: 3.45; 35: 0.37
C-5 |  |  | Medium vehicle | Central line + Before vehicle | 0.05 m | 4.09 | 0.41
C-6 |  | 25: 0.1 m; 30: 3.52; 35: 0.39
C-7 |  | 25: 0.15 m; 30: 3.41; 35: 0.39
C-8 | 9.0*9.0cm2 | 40cm | No vehicle | Central line | - | 9.45 | 0.5
C-9 |  |  | Small vehicle | Central line + Before vehicle | 0.05 m | 8.95 | 0.5
C-10 |  | 25: 0.1 m; 30: 8.91; 35: 0.5
C-11 |  | 25: 0.15 m; 30: 8.77; 35: 0.5
C-12 |  |  | Medium vehicle | Central line + Before vehicle | 0.05 m | 11.86 | 0.6
C-13 |  | 25: 0.1 m; 30: 11.03; 35: 0.59
C-14 |  | 25: 0.15 m; 30: 11.01; 35: 0.6
V'' - Dimensionless critical velocity and -Q'' Dimensionless heat release rate (2015 Chow)
Q'' | 0.0371 | 10.0021: 0.0451; 15: 0.0498
V'' | 0.2406 | 10.0021: 0.2799; 15: 0.3007
V'' - Non-dimensional critical velocity and Tilted angle (2015 Chow)
D = 0.16 | Angle | 10.0021: 2.996; 15: 6.0009
| V''cr | 10.0021: 1.0619; 15: 1.1488
D = 0.20 | Angle | 10.0021: 2.996; 15: 5.9964; 20: 9.0013
| V''cr | 10.0021: 1.0619; 15: 1.1258; 20: 1.1977
D = 0.26 | Angle | 10.0021: 0.0405; 15: 3.0004; 20: 5.9964; 25: 9.0058
| V''cr | 10.0021: 1.001; 15: 1.0686; 20: 1.1395; 25: 1.2125
Vcr- Critical velocity with S tunnel slope (2015-Chow)
5MW | S/% | 0 | 2 | 4 | 5 | 6
| Vcr/(m/s) | 1.4842 | 1.6406 | 1.663 | 1.6855 | 1.7195
10MW | S/% | 0 | 2 | 4 | 5 | 6
| Vcr/(m/s) | 1.778 | 1.9017 | 1.991 | 2.0251 | 2.0562
20MW | S/% | 0 | 2 | 4 | 5 | 6
| Vcr/(m/s) | 2.1047 | 2.2412 | 2.3662 | 2.3974 | 2.4414
30MW | S/% | 0 | 2 | 4 | 5 | 6
| Vcr/(m/s) | 2.3073 | 2.4637 | 2.5774 | 2.6328 | 2.701
50MW | S/% | 0 | 2 | 4 | 5 | 6
| Vcr/(m/s) | 2.5554 | 2.7376 | 2.8612 | 2.9281 | 3.0063
100MW | S/% | 0 | 2 | 4 | 5 | 6
| Vcr/(m/s) | 2.8251 | 3.0629 | 3.2207 | 3.299 | 3.3772
Vcr- Critical velocity with Ceiling exhaust velocity (2018-Tang)
1.5 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.3905 | 0.3811 | 0.3794 | 0.3709 | 0.3607 | 0.3505 | 0.3309 | 0.3104 | 0.2899 | 0.261
3.0 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.4886 | 0.4894 | 0.48 | 0.48 | 0.4707 | 0.4613 | 0.44 | 0.4306 | 0.411 | 0.3905
4.5 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.5602 | 0.5508 | 0.5406 | 0.5406 | 0.5312 | 0.5312 | 0.5107 | 0.491 | 0.48 | 0.4613
6.0 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.6105 | 0.6002 | 0.6011 | 0.5909 | 0.5806 | 0.5602 | 0.5499 | 0.5312 | 0.521 | 0.5116
7.5 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.6505 | 0.6505 | 0.6411 | 0.6411 | 0.6309 | 0.6207 | 0.6011 | 0.5909 | 0.5712 | 0.561
9.0 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.6914 | 0.6905 | 0.6804 | 0.671 | 0.6608 | 0.6407 | 0.6313 | 0.6207 | 0.6011 | 0.5913
10.5 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.7307 | 0.7217 | 0.7115 | 0.7012 | 0.7004 | 0.6914 | 0.671 | 0.6602 | 0.6514 | 0.651
12.0 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.7609 | 0.7409 | 0.7307 | 0.7204 | 0.7119 | 0.7017 | 0.6833 | 0.6723 | 0.671 | 0.671
13.5 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.7801 | 0.7715 | 0.7609 | 0.7417 | 0.7307 | 0.7119 | 0.7021 | 0.6919 | 0.6905 | 0.6905
15.0 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.8108 | 0.8014 | 0.7912 | 0.7699 | 0.7588 | 0.7503 | 0.7405 | 0.7204 | 0.72 | 0.7204
16.5 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.821 | 0.8112 | 0.7912 | 0.7818 | 0.7724 | 0.7622 | 0.752 | 0.7294 | 0.72 | 0.7204
18.0 kW | exhaust velocity | -0.0027828 | 0.2979 | 0.5985 | 0.8971 | 1.1978 | 1.4985 | 1.7992 | 2.0957 | 2.4005 | 2.697
| Vcr | 0.8108 | 0.801 | 0.7912 | 0.7801 | 0.7711 | 0.752 | 0.7412 | 0.7217 | 0.7302 | 0.7204
v*- Critical velocity with Q* Heat release rate (2018-Tang)
Experiments based on H | Q* | 0.0102 | 0.0203 | 0.0304 | 0.0405 | 0.0509 | 0.0607 | 0.0711 | 0.0812 | 0.0916 | 0.1017 | 0.1124 | 0.1222 | 0.1323 | 0.1421
| v* | 0.188 | 0.2359 | 0.2702 | 0.2939 | 0.3128 | 0.3325 | 0.351 | 0.3659 | 0.3756 | 0.3896 | 0.3944 | 0.3944 | 0.3949 | 0.3949
Experiments based on H | Q* | 0.0141 | 0.0287 | 0.043 | 0.0574 | 0.072 | 0.086 | 0.1006 | 0.1146 | 0.1292 | 0.1435 | 0.1575 | 0.1718 | 0.1864 | 0.2008
| v* | 0.2012 | 0.2526 | 0.2886 | 0.3149 | 0.3352 | 0.3558 | 0.3764 | 0.3918 | 0.4022 | 0.4177 | 0.423 | 0.423 | 0.423 | 0.423
V**- Dimensionless critical velocity with Q** dimensionless heat release rate (2018-Tang)
0 g/s | Q** | 0.0133 | 0.0269 | 0.0546 | 0.0401 | 0.069 | 0.0815 | 0.0955 | 0.1092 | 0.1237 | 0.1379 | 0.1511 | 0.1643 | 0.1801 | 0.1974
| V** | 0.2014 | 0.253 | 0.315 | 0.2892 | 0.3352 | 0.3568 | 0.3771 | 0.3921 | 0.4032 | 0.4183 | 0.4241 | 0.4173 | 0.4241 | 0.4231
10.2 g/s | Q** | 0.0104 | 0.0224 | 0.035 | 0.0468 | 0.0594 | 0.0722 | 0.0822 | 0.0864 | 0.0983 | 0.1258 | 0.1301 | 0.1518
| V** | 0.1912 | 0.2484 | 0.2788 | 0.305 | 0.331 | 0.3454 | 0.3568 | 0.3634 | 0.3706 | 0.4032 | 0.3976 | 0.4027
20.5 g/s | Q** | 0.0074366 | 0.0177 | 0.0401 | 0.0635 | 0.0932 | 0.1013 | 0.1367 | 0.1247 | 0.029 | 0.0515 | 0.0763 | 0.1118
| V** | 0.1705 | 0.227 | 0.2833 | 0.3246 | 0.3494 | 0.3617 | 0.3805 | 0.3867 | 0.2631 | 0.3092 | 0.3454 | 0.3841
30.8 g/s | Q** | 0.004415 | 0.0129 | 0.0326 | 0.0429 | 0.0539 | 0.0983 | 0.1105 | 0.1206 | 0.0759 | 0.0645 | 0.0879
| V** | 0.134 | 0.2011 | 0.2628 | 0.2886 | 0.3043 | 0.3706 | 0.3714 | 0.3719 | 0.3458 | 0.336 | 0.3551

## Database_critical velocity
Calculation ways for flame length
[15 empty] | V | Visual value
[15 empty] | F | Function of
Scale factor | L [m] | W [m] | H [m] | Fire source | Burner size | Fire location | Q [kW] | Q* | Lb [m] | slope | V [m/s] | V* | Ref | Remarks
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.4318 | - | 0.244 | - | 0.2566 | - | [1] |  | Flame location
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.7174 | - | 0.244 | - | 0.3032 | - | [1] |  | C | Center
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 1.4485 | - | 0.244 | - | 0.3785 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 2.906 | - | 0.244 | - | 0.4607 | - | [1] |  | Lb | Backing up distance
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 7.2684 | - | 0.244 | - | 0.5167 | - | [1] |  | V | ventilation velocity
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 14.3807 | - | 0.244 | - | 0.5192 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 29.0107 | - | 0.244 | - | 0.514 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.4318 | - | 0.732 | - | 0.2091 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.7174 | - | 0.732 | - | 0.2624 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 1.4485 | - | 0.732 | - | 0.3226 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 2.906 | - | 0.732 | - | 0.3988 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 7.2684 | - | 0.732 | - | 0.4539 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 14.3807 | - | 0.732 | - | 0.4584 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 29.0107 | - | 0.732 | - | 0.4493 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.4318 | - | 1.22 | - | 0.1679 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.7174 | - | 1.22 | - | 0.2214 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 1.4485 | - | 1.22 | - | 0.282 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 2.906 | - | 1.22 | - | 0.3383 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 7.2684 | - | 1.22 | - | 0.4027 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 14.3807 | - | 1.22 | - | 0.4149 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 29.0107 | - | 1.22 | - | 0.4087 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.4318 | - | 2.44 | - | 0.1202 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 0.7174 | - | 2.44 | - | 0.1726 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 1.4485 | - | 2.44 | - | 0.2154 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 2.906 | - | 2.44 | - | 0.2898 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 7.2684 | - | 2.44 | - | 0.3216 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | 14.3807 | - | 2.44 | - | 0.3348 | - | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | - | 0.0133 | 0 | - | - | 0.1792 | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | - | 0.022 | 0 | - | - | 0.2106 | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | - | 0.044 | 0 | - | - | 0.2628 | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | - | 0.088 | 0 | - | - | 0.3197 | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | - | 0.22 | 0 | - | - | 0.3523 | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | - | 0.44 | 0 | - | - | 0.3536 | [1]
- | 15 | 0.274 | 0.244 | Propane | 10cm × 10cm | Centre | - | 0.88 | 0 | - | - | 0.3472 | [1]
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | 130 mm height | - | 0.022 | 0 | - | - | 0.1504 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | 130 mm height | - | 0.044 | 0 | - | - | 0.2063 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | 130 mm height | - | 0.088 | 0 | - | - | 0.2561 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | 130 mm height | - | 0.22 | 0 | - | - | 0.3078 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | 130 mm height | - | 0.44 | 0 | - | - | 0.3143 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | 130 mm height | - | 0.88 | 0 | - | - | 0.3023 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.022 | 0 | - | - | 0.2574 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.044 | 0 | - | - | 0.3043 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.088 | 0 | - | - | 0.3559 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.22 | 0 | - | - | 0.3787 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.44 | 0 | - | - | 0.3877 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.88 | 0 | - | - | 0.3894 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.022 | 0 | - | - | 0.2099 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.044 | 0 | - | - | 0.2586 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.088 | 0 | - | - | 0.2988 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.22 | 0 | - | - | 0.3276 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.44 | 0 | - | - | 0.3245 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.022 | 0 | - | - | 0.139 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.044 | 0 | - | - | 0.1672 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.088 | 0 | - | - | 0.1954 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.22 | 0 | - | - | 0.217 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.44 | 0 | - | - | 0.2236 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.0133 | 0 | - | - | 0.1486 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.022 | 0 | - | - | 0.1848 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.044 | 0 | - | - | 0.222 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.088 | 0 | - | - | 0.282 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.22 | 0 | - | - | 0.3171 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.44 | 0 | - | - | 0.3201 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.88 | 0 | - | - | 0.3144 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.0133 | 0 | - | - | 0.1638 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.022 | 0 | - | - | 0.2009 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.044 | 0 | - | - | 0.2464 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.088 | 0 | - | - | 0.3174 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.22 | 0 | - | - | 0.3568 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.44 | 0 | - | - | 0.3653 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 4cm × 14cm | Centre | - | 0.88 | 0 | - | - | 0.3663 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | Centre | - | 0.022 | 0 | - | - | 0.1516 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | Centre | - | 0.044 | 0 | - | - | 0.2086 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | Centre | - | 0.088 | 0 | - | - | 0.2559 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | Centre | - | 0.22 | 0 | - | - | 0.3084 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | Centre | - | 0.44 | 0 | - | - | 0.3157 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 4mm × 236mm | Centre | - | 0.88 | 0 | - | - | 0.3014 | [1] | Longer side set across tunnel width
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Centre | - | 0.0221 | 0 | - | - | 0.1967 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Centre | - | 0.0441 | 0 | - | - | 0.2481 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Centre | - | 0.44 | 0 | - | - | 0.3719 | [1] | Longer side set along tunnel axis
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Beside wall | - | 0.0221 | 0 | - | - | 0.1854 | [1] | Burner set 10 mm from wall
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Beside wall | - | 0.0441 | 0 | - | - | 0.2372 | [1] | Burner set 10 mm from wall
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Beside wall | - | 0.088 | 0 | - | - | 0.3033 | [1] | Burner set 10 mm from wall
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Beside wall | - | 0.22 | 0 | - | - | 0.3484 | [1] | Burner set 10 mm from wall
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | Beside wall | - | 0.44 | 0 | - | - | 0.3618 | [1] | Burner set 10 mm from wall
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.0221 | 0 | - | - | 0.2596 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.0444 | 0 | - | - | 0.3045 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.088 | 0 | - | - | 0.3571 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.22 | 0 | - | - | 0.38 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.44 | 0 | - | - | 0.3879 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.88 | 0 | - | - | 0.3905 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.022 | 0 | - | - | 0.2594 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.044 | 0 | - | - | 0.305 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.088 | 0 | - | - | 0.355 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.22 | 0 | - | - | 0.38 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.44 | 0 | - | - | 0.3889 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.88 | 0 | - | - | 0.3885 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.022 | 0 | - | - | 0.2128 | [1] | 9% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.044 | 0 | - | - | 0.2591 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.088 | 0 | - | - | 0.2995 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.22 | 0 | - | - | 0.3284 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.44 | 0 | - | - | 0.3269 | [1] | 21% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.022 | 0 | - | - | 0.1418 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.044 | 0 | - | - | 0.1679 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.088 | 0 | - | - | 0.1961 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.22 | 0 | - | - | 0.2181 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 7cm × 8cm | 130 mm height | - | 0.44 | 0 | - | - | 0.224 | [1] | 37% blockage
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.244 | 0 | 0.6692 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.244 | 2 | 0.6923 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.244 | 4 | 0.697 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.244 | 6 | 0.7029 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.244 | 8 | 0.741 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.244 | 10 | 0.7572 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.244 | 0 | 0.6564 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.244 | 2 | 0.6762 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.244 | 4 | 0.6832 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.244 | 6 | 0.6914 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.244 | 8 | 0.7156 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.244 | 10 | 0.7388 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.244 | 0 | 0.5516 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.244 | 2 | 0.5403 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.244 | 4 | 0.613 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.244 | 6 | 0.5992 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.244 | 8 | 0.6097 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.244 | 10 | 0.6259 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.732 | 0 | 0.5929 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.732 | 2 | 0.6088 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.732 | 4 | 0.6259 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.732 | 6 | 0.6301 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.732 | 8 | 0.6625 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 0.732 | 10 | 0.662 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.732 | 0 | 0.5764 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.732 | 2 | 0.5735 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.732 | 4 | 0.6212 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.732 | 6 | 0.6231 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.732 | 8 | 0.6484 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 0.732 | 10 | 0.6491 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.732 | 0 | 0.479 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.732 | 2 | 0.4961 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.732 | 4 | 0.5213 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.732 | 6 | 0.5268 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.732 | 8 | 0.5356 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 0.732 | 10 | 0.5423 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 1.22 | 0 | 0.5102 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 1.22 | 2 | 0.5524 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 1.22 | 4 | 0.5689 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 1.22 | 6 | 0.5713 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 1.22 | 8 | 0.5918 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 1.22 | 10 | 0.6014 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 1.22 | 0 | 0.4898 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 1.22 | 2 | 0.5168 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 1.22 | 4 | 0.5455 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 1.22 | 6 | 0.5585 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 1.22 | 8 | 0.5574 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 1.22 | 10 | 0.5786 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 1.22 | 0 | 0.4319 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 1.22 | 2 | 0.4536 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 1.22 | 4 | 0.4794 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 1.22 | 6 | 0.4689 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 1.22 | 8 | 0.4755 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 1.22 | 10 | 0.4774 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 2.44 | 0 | 0.3885 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 2.44 | 2 | 0.4635 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 2.44 | 4 | 0.4642 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 2.44 | 6 | 0.4748 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 2.44 | 8 | 0.4863 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.44 | 2.44 | 10 | 0.4653 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 2.44 | 0 | 0.3791 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 2.44 | 2 | 0.4386 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 2.44 | 4 | 0.4501 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 2.44 | 6 | 0.4466 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 2.44 | 8 | 0.4485 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.22 | 2.44 | 10 | 0.4487 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 2.44 | 0 | 0.3143 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 2.44 | 2 | 0.3727 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 2.44 | 4 | 0.3735 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 2.44 | 6 | 0.3689 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 2.44 | 8 | 0.3684 | - | [2]
- | 15 | 0.274 | 0.244 | Propane | 100 mm diameter | Centre | - | 0.088 | 2.44 | 10 | 0.3734 | - | [2]
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 1.5 | 0.108 | 0 | - | 0.43 | 0.333 | [3] | hydraulic tunnel height
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 3 | 0.216 | 0 | - | 0.46 | 0.356 | [3] | hydraulic tunnel height
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 7.5 | 0.539 | 0 | - | 0.48 | 0.372 | [3] | hydraulic tunnel height
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 10.5 | 0.754 | 0 | - | 0.48 | 0.372 | [3] | hydraulic tunnel height
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 12 | 0.862 | 0 | - | 0.48 | 0.372 | [3] | hydraulic tunnel height
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 15 | 1.078 | 0 | - | 0.48 | 0.372 | [3] | hydraulic tunnel height
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 22.5 | 1.616 | 0 | - | 0.48 | 0.372 | [3] | hydraulic tunnel height
1:10 | 15 | 0.136 | 0.25 | Propane | 106 mm diameter | Centre | 30 | 2.155 | 0 | - | 0.48 | 0.372 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 1.5 | 0.041 | 0 | - | 0.39 | 0.248 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 3 | 0.082 | 0 | - | 0.48 | 0.309 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 7.5 | 0.205 | 0 | - | 0.56 | 0.354 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 10.5 | 0.288 | 0 | - | 0.59 | 0.379 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 12 | 0.329 | 0 | - | 0.6 | 0.382 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 15 | 0.411 | 0 | - | 0.6 | 0.382 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 22.5 | 0.616 | 0 | - | 0.6 | 0.382 | [3] | hydraulic tunnel height
1:10 | 15 | 0.25 | 0.25 | Propane | 106 mm diameter | Centre | 30 | 0.822 | 0 | - | 0.6 | 0.382 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 1.5 | 0.021 | 0 | - | 0.37 | 0.203 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 3 | 0.041 | 0 | - | 0.45 | 0.251 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 7.5 | 0.103 | 0 | - | 0.54 | 0.298 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 10.5 | 0.144 | 0 | - | 0.57 | 0.319 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 12 | 0.164 | 0 | - | 0.59 | 0.325 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 15 | 0.205 | 0 | - | 0.6 | 0.332 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 22.5 | 0.308 | 0 | - | 0.62 | 0.344 | [3] | hydraulic tunnel height
1:10 | 15 | 0.5 | 0.25 | Propane | 106 mm diameter | Centre | 30 | 0.41 | 0 | - | 0.65 | 0.359 | [3] | hydraulic tunnel height
1:10 | 15 | 1 | 0.25 | Propane | 106 mm diameter | Centre | 1.5 | 0.01 | 0 | - | 0.34 | 0.162 | [3] | hydraulic tunnel height
1:10 | 15 | 1 | 0.25 | Propane | 106 mm diameter | Centre | 3 | 0.02 | 0 | - | 0.4 | 0.192 | [3] | hydraulic tunnel height
1:10 | 15 | 1 | 0.25 | Propane | 106 mm diameter | Centre | 7.5 | 0.05 | 0 | - | 0.5 | 0.241 | [3] | hydraulic tunnel height
1:10 | 15 | 1 | 0.25 | Propane | 106 mm diameter | Centre | 10.5 | 0.07 | 0 | - | 0.54 | 0.259 | [3] | hydraulic tunnel height
1:10 | 15 | 1 | 0.25 | Propane | 106 mm diameter | Centre | 12 | 0.08 | 0 | - | 0.56 | 0.27 | [3] | hydraulic tunnel height
1:10 | 15 | 1 | 0.25 | Propane | 106 mm diameter | Centre | 15 | 0.1 | 0 | - | 0.59 | 0.284 | [3] | hydraulic tunnel height
1:10 | 15 | 1 | 0.25 | Propane | 106 mm diameter | Centre | 22.5 | 0.15 | 0 | - | 0.65 | 0.313 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 1.5 | 0.046 | 0 | - | 0.44 | 0.288 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 3 | 0.093 | 0 | - | 0.54 | 0.353 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 7.5 | 0.232 | 0 | - | 0.6 | 0.393 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 10.5 | 0.325 | 0 | - | 0.6 | 0.393 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 12 | 0.372 | 0 | - | 0.6 | 0.393 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 15 | 0.465 | 0 | - | 0.6 | 0.393 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 22.5 | 0.67 | 0 | - | 0.6 | 0.393 | [3] | hydraulic tunnel height
1:10 | 15 | 0.274 | 0.244 | Propane | 106 mm diameter | Centre | 30 | 0.929 | 0 | - | 0.6 | 0.393 | [3] | hydraulic tunnel height

## Reference lists
Ref. No | Title
1 | Oka Y, Atkinson GT. Control of Smoke Flow in Tunnel Fires. Fire Saf J 1995;25:305–22. (Oka et al. 1995 )
2 | Atkinson G., Wu Y. Short Control in Sloping Tunnels. Fire Saf J 1997;27:335–41. (Atkinson et al. 1997 )
3 | Control of smoke flow in tunnel fires using longitudinal ventilation systems - a study of the critical velocity. (Wu et al. 2000 )
4 | Parametrical study of the back flow occurrence in case of a buoyant release into a rectangular channel. (Vauquelin 2005 )
5 | Influence of tunnel width on longitudinal smoke control. (Vauquelin et al. 2006)
6 | An experimental study on the effect of ventilation velocity on burning rate in tunnel fires — heptane pool fire case. (Roh et al. 2008)
7 | Studies on buoyancy-driven back-layering flow in tunnel fires (Hu et al. 2008)
8 | Study of critical velocity and backlayering length in longitudinally ventilated tunnel fires. (Li et al. 2010)
9 | Critical ventilation velocity for tunnel fires occurring near tunnel exits. (Tsai et al. 2011)
10 | Effect of vehicular blockage on critical ventilation velocity and tunnel fire behavior in longitudinally ventilated tunnels. (Lee et al. 2012)
11 | An Experimental Study of the Effect of the Aspect Ratio on the Critical Velocity in Longitudinal Ventilation Tunnel Fires. (Lee et al. 2015)
12 | Smoke movement in tilted tunnel fires with longitudinal ventilation.(Chow et al. 2015)
13 | Effect of ceiling centralized mechanical smoke exhaust on the critical velocity that inhibits the reverse flow of thermal plume in a longitudinal ventilated tunnel. (Tang et al. 2018)
14 | Prediction of backlayering length and critical velocity in metro tunnel fire (Weng et al. 2015)
15 | An experimental investigation on blockage effect of metro train on the smoke back-layering in subway tunnel fires (Zhang et al. 2016)
16 | Effect of ceiling centralized mechanical smoke exhaust on the critical velocity that inhibits the reverse flow of thermal plume in a longitudinal ventilated tunnel (Tang et al. 2018)
17 | Influence of ambient pressure on critical ventilation velocity and backlayering distance of thermal driven smoke in tunnels with longitudinal ventilation (Guo et al. 2019)