## 3.3 Ceiling temperature
1. Maximum temperature and flame extension length in a longitudinal ventilated tunnel (2019 Longfei Chen)
Tunnel information
Scale | 1:10 |  | Fire source | Fire size
Length | 16.5 |  | LPG | 64
Width | 1.3 |  |  | 80
Height | 0.65 |  |  | 96
112
128
144
64 kW | Distance | H=0.3m | -42.1978 | -35.2747 | -31.3187 | -26.044 | -16.1538 | 0 | 6.2637 | 11.8681 | 16.8132 | 20.7692 | 24.7253 | 31.6484 | 35.9341 | 41.2088 | 47.1429 | 51.0989
| Temp[K] |  | 462.305 | 588.785 | 693.458 | 763.24 | 907.165 | 1094.7 | 1068.54 | 972.586 | 902.804 | 876.636 | 841.745 | 776.324 | 728.349 | 671.651 | 532.087 | 453.583
|  | 0.35 | -42.1978 | -34.9451 | -31.3187 | -26.044 | -16.4835 | 0.32967 | 5.9341 | 11.8681 | 16.8132 | 20.7692 | 24.7253 | 31.6484 | 35.9341 | 41.2088 | 46.4835 | 51.4286
|  |  | 423.053 | 527.726 | 662.928 | 732.71 | 841.745 | 1112.15 | 1038.01 | 937.695 | 850.467 | 815.576 | 785.047 | 750.156 | 693.458 | 632.399 | 532.087 | 449.221
|  | 0.4 | -42.1978 | -35.2747 | -31.3187 | -26.044 | -16.4835 | 0 | 5.9341 | 11.8681 | 16.8132 | 20.7692 | 24.7253 | 31.978 | 35.9341 | 40.8791 | 46.8132 | 51.0989
|  |  | 383.801 | 492.835 | 632.399 | 706.542 | 763.24 | 1077.26 | 1020.56 | 902.804 | 750.156 | 706.542 | 684.735 | 654.206 | 658.567 | 597.508 | 462.305 | 401.246
144 kW | Distance | H=0.3m | -41.7543 | -35.0342 | -30.5758 | -26.1205 | -15.9468 | 0.26356 | 5.968 | 11.9909 | 17.3828 | 21.1835 | 24.9871 | 32.2808 | 35.7581 | 41.1391 | 47.4508 | 51.2396
| Temp[K] |  | 663.591 | 899.35 | 960.571 | 1008.71 | 1074.5 | 1162.31 | 1118.91 | 1079.88 | 1058.26 | 1019.15 | 993.12 | 958.494 | 893.2 | 823.614 | 658.111 | 566.66
|  | 0.35 | -42.0955 | -35.0836 | -31.2177 | -26.1244 | -15.9557 | 0.5741 | 6.2815 | 12.3054 | 17.3759 | 21.496 | 25.2927 | 31.9396 | 36.0538 | 41.1223 | 47.4558 | 51.5551
|  |  | 558.906 | 681.279 | 930.018 | 991.262 | 1035.25 | 1131.8 | 1101.47 | 1066.8 | 1027.73 | 997.354 | 940.795 | 853.809 | 797.261 | 749.47 | 679.918 | 557.949
|  | 0.4 | -42.0985 | -35.0856 | -30.9299 | -26.1541 | -15.9626 | 0.2517 | 6.2776 | 12.2985 | 17.3601 | 21.4742 | 25.2759 | 32.5667 | 36.0439 | 41.1095 | 47.1284 | 51.2287
|  |  | 545.822 | 672.557 | 799.187 | 860.42 | 1004.72 | 1109.98 | 1084.03 | 1036.27 | 957.952 | 901.404 | 866.651 | 818.941 | 753.646 | 692.771 | 636.292 | 518.684
H [m] | kW | Max Temp.
0.3 | 63.7683 | 1068.46
| 79.6367 | 1073.85
| 95.7266 | 1060.38
| 111.817 | 1044.2
| 127.9 | 1063.07
| 143.986 | 1065.77
0.35 | 63.9804 | 1092.72
| 79.6355 | 1079.25
| 95.7178 | 1100.81
| 111.807 | 1090.03
| 127.897 | 1076.55
| 143.987 | 1060.38
0.4 | 63.9921 | 1038.81
| 79.6349 | 1081.94
| 95.7225 | 1079.25
| 111.81 | 1076.55
| 127.892 | 1100.81
| 143.983 | 1079.25
ventilation
Q | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp.
64 kW | 0 | -42.3077 | 459.701 | 0.3 | -41.9231 | 397.015 | 0.6 | -42.3077 | 362.189 | 0.9 | -42.3077 | 306.468 | 1.2 | -41.9231 | 299.502 | 1.5 | -41.9231 | 306.468
|  | -34.6154 | 585.075 |  | -35 | 473.632 |  | -35 | 410.945 |  | -35.3846 | 334.328 |  | -35 | 313.433 |  | -34.2308 | 299.502
|  | -30.7692 | 703.483 |  | -30.7692 | 522.388 |  | -30.7692 | 445.771 |  | -31.1538 | 341.294 |  | -30.7692 | 299.502 |  | -30.7692 | 292.537
|  | -26.1538 | 766.169 |  | -26.1538 | 592.04 |  | -26.1538 | 459.701 |  | -25.7692 | 362.189 |  | -25.7692 | 299.502 |  | -25.7692 | 285.572
|  | -16.1538 | 905.473 |  | -16.1538 | 647.761 |  | -16.1538 | 508.458 |  | -16.1538 | 424.876 |  | -16.1538 | 327.363 |  | -16.1538 | 320.398
|  | 0 | 1093.53 |  | 0 | 926.368 |  | 0 | 654.726 |  | 0 | 515.423 |  | -0.38461 | 341.294 |  | 0 | 327.363
|  | 5.7692 | 1030.85 |  | 5.7692 | 940.299 |  | 5.7692 | 703.483 |  | 6.1539 | 543.284 |  | 5.7692 | 348.259 |  | 6.1539 | 327.363
|  | 11.9231 | 975.124 |  | 11.9231 | 905.473 |  | 11.9231 | 773.134 |  | 12.3077 | 585.075 |  | 11.9231 | 348.259 |  | 11.9231 | 341.294
|  | 17.3077 | 905.473 |  | 16.9231 | 842.786 |  | 16.9231 | 773.134 |  | 16.9231 | 599.005 |  | 16.5385 | 341.294 |  | 17.3077 | 327.363
|  | 20.7692 | 870.647 |  | 21.1538 | 828.856 |  | 21.1538 | 814.925 |  | 20.7692 | 633.831 |  | 20.7692 | 348.259 |  | 21.1538 | 334.328
|  | 25.3846 | 849.751 |  | 25 | 787.065 |  | 25.3846 | 807.96 |  | 25 | 640.796 |  | 24.6154 | 355.224 |  | 25 | 327.363
|  | 31.9231 | 780.1 |  | 31.9231 | 745.274 |  | 31.9231 | 766.169 |  | 32.3077 | 668.657 |  | 31.9231 | 403.98 |  | 31.9231 | 327.363
|  | 36.1538 | 745.274 |  | 36.1538 | 717.413 |  | 36.1538 | 731.343 |  | 35.7692 | 696.517 |  | 36.5385 | 431.841 |  | 35.7692 | 334.328
|  | 41.5385 | 668.657 |  | 41.1538 | 668.657 |  | 41.5385 | 703.483 |  | 41.5385 | 661.692 |  | 41.5385 | 480.597 |  | 41.1538 | 348.259
|  | 46.9231 | 501.493 |  | 47.3077 | 585.075 |  | 46.9231 | 612.935 |  | 46.9231 | 585.075 |  | 47.3077 | 459.701 |  | 47.3077 | 355.224
|  | 51.1538 | 431.841 |  | 51.5385 | 473.632 |  | 51.1538 | 487.562 |  | 51.1538 | 508.458 |  | 51.1538 | 438.806 |  | 51.1538 | 355.224
Q | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp.
112 kW | 0 | -41.9232 | 518 | 0.3 | -42.3596 | 462 | 0.6 | -42.404 | 385 | 0.9 | -42.0121 | 364 | 1.2 | -42.0485 | 301 | 1.5 | -41.6444 | 301
|  | -34.5737 | 651 |  | -35.0303 | 560 |  | -35.0949 | 448 |  | -34.7111 | 413 |  | -35.1758 | 308 |  | -34.7758 | 301
|  | -30.4848 | 735 |  | -30.9455 | 637 |  | -31.0222 | 504 |  | -31.0586 | 441 |  | -31.1394 | 301 |  | -31.1434 | 294
|  | -25.9879 | 826 |  | -26.0485 | 721 |  | -26.1657 | 518 |  | -26.2061 | 448 |  | -26.2909 | 301 |  | -25.8909 | 294
|  | -15.4141 | 945 |  | -15.5071 | 784 |  | -15.6323 | 567 |  | -15.6768 | 490 |  | -15.7697 | 329 |  | -15.7737 | 322
|  | 0.43636 | 1106 |  | 0.79192 | 1022 |  | -0.17374 | 749 |  | 0.13737 | 588 |  | -0.0080808 | 336 |  | 0.80404 | 343
|  | 6.0687 | 1064 |  | 6.4687 | 1057 |  | 6.3475 | 847 |  | 6.2303 | 644 |  | 6.0606 | 350 |  | 5.6525 | 343
|  | 12.9091 | 1015 |  | 12.4929 | 994 |  | 12.4404 | 903 |  | 11.9111 | 686 |  | 12.1333 | 371 |  | 12.1253 | 357
|  | 17.3333 | 980 |  | 17.3131 | 945 |  | 17.701 | 917 |  | 17.1677 | 693 |  | 16.9778 | 364 |  | 16.9657 | 343
|  | 25.3535 | 875 |  | 25.7737 | 903 |  | 21.7455 | 924 |  | 20.8323 | 742 |  | 21.0384 | 399 |  | 21.0101 | 350
|  | 32.1616 | 770 |  | 36.5737 | 714 |  | 25.7939 | 938 |  | 25.6889 | 756 |  | 25.4909 | 413 |  | 24.6424 | 343
|  | 36.1939 | 756 |  | 40.9939 | 672 |  | 32.2384 | 903 |  | 36.2303 | 819 |  | 32 | 490 |  | 32.3354 | 371
|  | 41.4222 | 714 |  | 47.4465 | 651 |  | 36.6424 | 833 |  | 41.4788 | 812 |  | 36.0646 | 532 |  | 36.3798 | 378
|  | 47.4303 | 623 |  | 51.4101 | 518 |  | 41.0667 | 798 |  | 47.4747 | 700 |  | 40.9535 | 602 |  | 41.2485 | 413
|  | 51.402 | 504 |  |  |  |  | 47.0949 | 742 |  | 51.4667 | 616 |  | 47.398 | 567 |  | 47.3212 | 434
[8 empty] | 51.4465 | 581 |  |  |  |  | 51.4263 | 546 |  | 50.9576 | 434
Q | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp. | V | Distance from fire | Temp.
144 kW | 0 | -42.069 | 547.404 | 0.3 | -42.064 | 528.049 | 0.6 | -42.0357 | 418.37 | 0.9 | -42.0257 | 379.659 | 1.2 | -42.0091 | 315.142 | 1.5 | -42.0074 | 308.691
|  | -35.2365 | 682.52 |  | -34.8683 | 656.694 |  | -35.1832 | 476.066 |  | -34.8084 | 424.433 |  | -35.1432 | 321.225 |  | -35.1415 | 314.773
|  | -31.2921 | 804.889 |  | -31.2788 | 753.275 |  | -30.8557 | 514.543 |  | -31.1955 | 430.69 |  | -31.1639 | 308.108 |  | -31.1622 | 301.656
|  | -26.2468 | 862.682 |  | -26.2435 | 849.779 |  | -26.1685 | 559.452 |  | -25.4223 | 469.089 |  | -25.7421 | 307.816 |  | -26.1019 | 301.384
|  | -15.7997 | 997.604 |  | -16.1429 | 926.655 |  | -16.0629 | 616.973 |  | -16.0379 | 520.198 |  | -15.9896 | 333.098 |  | -15.9913 | 339.55
|  | -0.28566 | 1106.45 |  | 0.072457 | 1119.33 |  | 0.15241 | 809.65 |  | 0.20405 | 609.647 |  | -0.087448 | 338.695 |  | -0.085782 | 332.243
|  | 5.8673 | 1073.86 |  | 5.8607 | 1099.67 |  | 5.9073 | 919.018 |  | 5.6008 | 706.131 |  | 5.6891 | 364.191 |  | 6.4153 | 351.249
|  | 12.022 | 1034.82 |  | 12.0153 | 1060.62 |  | 11.6755 | 976.772 |  | 12.0936 | 757.395 |  | 12.55 | 389.628 |  | 11.8338 | 363.86
|  | 17.104 | 950.674 |  | 16.7208 | 1034.57 |  | 17.0956 | 982.932 |  | 16.7991 | 731.335 |  | 16.5276 | 382.963 |  | 16.5376 | 344.253
|  | 21.0916 | 905.298 |  | 21.0782 | 956.912 |  | 21.0699 | 989.17 |  | 20.7601 | 789.187 |  | 21.2148 | 427.872 |  | 20.8717 | 356.923
|  | 24.7177 | 859.942 |  | 25.0675 | 905.084 |  | 25.0409 | 1008.31 |  | 24.7311 | 808.328 |  | 25.1825 | 459.917 |  | 25.2108 | 350.238
|  | 31.9584 | 814.391 |  | 32.3199 | 814.372 |  | 31.9134 | 988.587 |  | 31.9518 | 840.198 |  | 32.3882 | 549.852 |  | 32.4298 | 388.56
|  | 35.9527 | 743.209 |  | 36.3075 | 768.996 |  | 35.5346 | 962.586 |  | 36.2808 | 872.224 |  | 35.9843 | 620.627 |  | 36.3991 | 414.153
|  | 41.3878 | 691.304 |  | 41.018 | 723.582 |  | 41.3345 | 897.758 |  | 41.3428 | 865.5 |  | 41.0297 | 678.42 |  | 40.7265 | 452.63
|  | 47.186 | 632.928 |  | 47.1743 | 678.089 |  | 47.1327 | 839.382 |  | 47.5191 | 742.587 |  | 47.191 | 613.572 |  | 46.8662 | 471.654
|  | 51.555 | 510.112 |  | 51.545 | 548.822 |  | 51.5151 | 664.953 |  | 50.7922 | 664.992 |  | 51.1736 | 587.552 |  | 51.565 | 471.402
2. Maximum temperature beneath the ceiling (2011 Ying Zhen Li )
Tunnel information
Scale | 1:23 |  | Fire source | Fire size
Length | 12 |  | porous bed nurner | 2-15 [kW]
Width | 0.25
Height | 0.25
Ventilation velocity
| Q | V | Tmax |  | Q | V | Tmax
| 4.3 | 0.7 | 216.5 |  | 2 | 0.33 | 53.9
| 4.3 | 0.59 | 256 |  | 2 | 0.36 | 49.1
| 4.3 | 0.36 | 296 |  | 2 | 0.38 | 45.8
| 5.2 | 0.69 | 271.2 |  | 3.5 | 0.41 | 89.4
| 5.2 | 0.59 | 313.1 |  | 3.5 | 0.43 | 77.7
| 5.2 | 0.34 | 358.7 |  | 3.5 | 0.45 | 72.8
| 6 | 0.72 | 297.2 |  | 4.6 | 0.43 | 106.8
| 6 | 0.66 | 321.8 |  | 4.6 | 0.45 | 95
| 6 | 0.58 | 360.8 |  | 4.6 | 0.49 | 97.3
| 6 | 0.48 | 363.5 |  | 4.6 | 0.53 | 88.5
| 1.1 | 0.11 | 143.8 |  | 2.4 | 0.1 | 130.9
| 1.2 | 0.05 | 202.7 |  | 2.4 | 0.12 | 129.8
| 1.9 | 0.13 | 349.1 |  | 5.9 | 0.09 | 290.1
| 4.3 | 0.08 | 463.1 |  | 5.9 | 0.13 | 287.7
[5 empty] | 7.5 | 0.11 | 335.6
[5 empty] | 7.5 | 0.2 | 310
[5 empty] | 7.5 | 0.23 | 330
[5 empty] | 11.5 | 0.05 | 451
[5 empty] | 14 | 0.1 | 492.2
[5 empty] | 11.5 | 0.12 | 437.1
3. Transverse Maximum temperature in road tunnel (2013 C. G. Fan et al. )
Tunnel information
Scale | 1:6 |  | Fire source | Fire size
Length | 6 |  | Methanol | 3.38-29.57 | [kW]
Width | 2
Height | 0.88
Distance | HRR
1 | 3.38 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 12.3286 | 15.4376 | 17.0036 | 21.6776 | 29.4357 | 29.9609 | 40.7877 | 51.6011 | 56.2502 | 44.4861 | 30.6672 | 22.4999 | 17.4138
| 4.93 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 15.9245 | 18.5188 | 21.1141 | 25.7872 | 34.5698 | 36.1262 | 49.5214 | 63.4189 | 71.1473 | 55.2756 | 37.3462 | 26.0967 | 22.038
| 6.95 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 22.6034 | 26.7379 | 29.8449 | 36.5756 | 48.957 | 52.0506 | 71.6083 | 90.1271 | 97.8583 | 76.3331 | 50.7012 | 36.3696 | 30.2561
| 9.44 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 29.2824 | 34.4442 | 37.5522 | 44.7957 | 59.2308 | 61.8098 | 80.8547 | 103.999 | 113.27 | 90.2057 | 63.0317 | 47.159 | 40.0201
| 12.56 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 34.4193 | 39.0674 | 43.2028 | 51.9854 | 68.4734 | 73.112 | 95.2372 | 113.758 | 122.515 | 97.9082 | 69.1932 | 52.8068 | 44.6395
| 16.45 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 42.6384 | 47.7992 | 52.963 | 64.3141 | 86.9683 | 88.5208 | 117.842 | 142.525 | 150.767 | 121.025 | 83.5756 | 62.566 | 52.3458
| 20.21 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 49.8291 | 56.533 | 62.7241 | 75.6182 | 99.2988 | 102.392 | 131.197 | 157.423 | 166.178 | 135.921 | 96.4198 | 72.8436 | 62.104
| 23.8 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 55.4807 | 61.6699 | 68.8846 | 82.2942 | 108.03 | 113.18 | 144.553 | 172.835 | 183.131 | 155.957 | 113.375 | 83.1194 | 69.8123
| 29.57 | x | 0 | 0.10371 | 0.20065 | 0.39818 | 0.60301 | 0.64776 | 0.80021 | 0.90042 | 1.0009 | 1.1993 | 1.3977 | 1.5996 | 1.7976
|  | y | 65.7555 | 73.4858 | 81.7297 | 98.7314 | 126.012 | 132.186 | 168.183 | 195.435 | 204.705 | 178.56 | 132.892 | 100.579 | 85.2221
0.75 | 3.38 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 18.3333 | 21.1111 | 24.4444 | 33.3333 | 48.3333 | 52.2222 | 59.4444 | 57.7778 | 43.3333 | 26.6667 | 18.8889 | 15.5556 | 13.8889
| 4.93 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 23.3333 | 28.3333 | 32.2222 | 40 | 62.2222 | 66.1111 | 72.7778 | 71.1111 | 52.7778 | 34.4444 | 25 | 21.6667 | 17.7778
| 6.95 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 31.1111 | 36.1111 | 41.1111 | 53.8889 | 78.3333 | 86.6667 | 94.4444 | 91.1111 | 69.4444 | 45.5556 | 32.7778 | 27.2222 | 24.4444
| 9.44 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 39.4444 | 45.5556 | 51.1111 | 65.5556 | 98.3333 | 104.444 | 114.444 | 110 | 83.3333 | 55 | 40.5556 | 35 | 31.1111
| 12.56 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 46.6667 | 53.8889 | 61.1111 | 78.8889 | 109.444 | 118.889 | 130 | 128.333 | 102.222 | 67.7778 | 50 | 42.7778 | 36.6667
| 16.45 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 55 | 61.1111 | 70 | 89.4444 | 129.444 | 137.778 | 149.444 | 146.111 | 115.556 | 77.2222 | 57.7778 | 47.7778 | 43.3333
| 20.21 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 59.4444 | 66.6667 | 76.6667 | 97.2222 | 139.444 | 148.333 | 158.333 | 154.444 | 129.444 | 85.5556 | 63.3333 | 53.3333 | 46.6667
| 23.8 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 68.8889 | 78.3333 | 90.5556 | 117.222 | 162.778 | 170 | 180.556 | 175.556 | 143.889 | 97.7778 | 72.2222 | 60.5556 | 54.4444
| 29.57 | x | 0.0024538 | 0.097436 | 0.20065 | 0.40687 | 0.59597 | 0.65358 | 0.73987 | 0.78971 | 0.99394 | 1.2025 | 1.402 | 1.6011 | 1.8
|  | y | 77.7778 | 88.3333 | 101.111 | 130.556 | 179.444 | 186.111 | 200.556 | 194.444 | 161.111 | 111.111 | 82.2222 | 68.8889 | 61.6667
0.5 | 3.38 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 26.1986 | 29.7945 | 31.8493 | 39.0411 | 51.3699 | 57.0205 | 52.3973 | 35.4452 | 24.6575 | 18.4932 | 15.411 | 12.3288 | 11.8151
| 4.93 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 35.9589 | 40.0685 | 42.1233 | 51.3699 | 65.7534 | 68.8356 | 60.6164 | 41.6096 | 30.8219 | 22.6027 | 18.4932 | 15.9247 | 14.8973
| 6.95 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 44.6918 | 47.2603 | 53.4247 | 64.726 | 85.274 | 88.8699 | 82.1918 | 55.4795 | 40.5822 | 30.8219 | 26.1986 | 21.5753 | 20.5479
| 9.44 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 54.4521 | 60.6164 | 64.2123 | 78.5959 | 102.74 | 109.418 | 101.199 | 69.3493 | 51.8836 | 38.0137 | 31.3356 | 27.226 | 25.1712
| 12.56 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 64.2123 | 70.8904 | 73.9726 | 89.8973 | 117.637 | 124.315 | 116.096 | 79.1096 | 59.0753 | 43.6644 | 36.9863 | 32.8767 | 29.7945
| 16.45 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 75.5137 | 81.6781 | 88.3562 | 107.877 | 139.726 | 150 | 140.753 | 99.1438 | 73.4589 | 54.4521 | 46.7466 | 40.5822 | 36.9863
| 20.21 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 85.274 | 93.4932 | 100.685 | 118.664 | 154.11 | 163.356 | 157.192 | 111.986 | 84.2466 | 63.6986 | 52.911 | 46.2329 | 43.1507
| 23.8 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 97.6027 | 105.822 | 114.041 | 135.616 | 175.685 | 186.986 | 181.849 | 131.507 | 100.685 | 75.5137 | 64.726 | 55.4795 | 50.8562
| 29.57 | x | 0.0086203 | 0.070826 | 0.10504 | 0.1983 | 0.39733 | 0.49686 | 0.59357 | 0.79653 | 0.9962 | 1.1958 | 1.4077 | 1.6009 | 1.7972
|  | y | 110.445 | 121.233 | 131.507 | 157.705 | 193.664 | 200.856 | 191.096 | 138.185 | 106.849 | 79.6233 | 67.8082 | 59.589 | 54.9658
0.4 | 3.38 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 32.5737 | 38.6059 | 44.0349 | 53.6863 | 54.8928 | 41.622 | 26.5416 | 21.1126 | 15.6836 | 12.6676 | 12.0643 | 11.4611 | 7.2386
| 4.93 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 41.0188 | 48.2574 | 57.3056 | 69.9732 | 76.0054 | 59.7185 | 39.8123 | 28.9544 | 21.7158 | 19.3029 | 15.6836 | 15.0804 | 10.8579
| 6.95 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 53.0831 | 62.7346 | 72.9893 | 84.4504 | 89.2761 | 71.1796 | 48.2574 | 36.193 | 29.5576 | 24.1287 | 21.1126 | 19.3029 | 14.4772
| 9.44 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 60.3217 | 72.9893 | 86.2601 | 104.96 | 114.611 | 95.3083 | 60.9249 | 44.0349 | 33.7802 | 29.5576 | 25.3351 | 24.1287 | 19.3029
| 12.56 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 75.4021 | 88.0697 | 102.547 | 115.214 | 118.231 | 97.7212 | 66.3539 | 50.6702 | 38.6059 | 33.7802 | 30.1609 | 28.3512 | 22.319
| 16.45 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 86.8633 | 104.357 | 121.85 | 137.534 | 144.772 | 119.437 | 81.4343 | 62.7346 | 48.2574 | 42.2252 | 37.3995 | 34.3834 | 27.748
| 20.21 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 98.3244 | 117.024 | 135.121 | 153.82 | 159.249 | 139.343 | 98.3244 | 76.0054 | 59.7185 | 51.8767 | 45.8445 | 43.4316 | 33.7802
| 23.8 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 118.834 | 141.153 | 160.456 | 179.155 | 182.172 | 150.201 | 106.166 | 87.4665 | 68.7668 | 59.7185 | 53.6863 | 48.8606 | 40.4155
| 29.57 | x | 0 | 0.10104 | 0.19747 | 0.30117 | 0.38677 | 0.60025 | 0.79229 | 1.006 | 1.1984 | 1.3943 | 1.5975 | 1.7972 | 2
|  | y | 132.708 | 157.44 | 183.378 | 199.665 | 205.697 | 169.504 | 120.643 | 95.3083 | 72.9893 | 63.3378 | 56.7024 | 53.0831 | 43.4316
0.3 | 3.38 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 42.7553 | 57.1853 | 60.3919 | 51.8409 | 34.7387 | 23.5154 | 19.7743 | 14.4299 | 12.8266 | 10.6888 | 10.1544 | 6.9477
| 4.93 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 50.772 | 67.8741 | 70.0119 | 64.6675 | 43.2898 | 30.4632 | 25.1188 | 19.7743 | 17.6366 | 14.4299 | 13.361 | 10.1544
| 6.95 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 64.6675 | 88.1829 | 90.8551 | 84.4418 | 59.323 | 40.0831 | 32.601 | 25.6532 | 21.9121 | 21.3777 | 19.2399 | 14.4299
| 9.44 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 81.7696 | 107.957 | 112.767 | 105.285 | 75.3563 | 51.8409 | 41.152 | 32.601 | 29.3943 | 26.1876 | 24.0499 | 19.2399
| 12.56 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 91.924 | 123.99 | 131.473 | 125.594 | 91.924 | 62.5297 | 49.1686 | 37.9454 | 33.6698 | 31.5321 | 28.3254 | 22.981
| 16.45 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 114.371 | 153.385 | 157.66 | 145.903 | 101.01 | 67.8741 | 52.9097 | 43.2898 | 37.9454 | 34.7387 | 32.601 | 26.1876
| 20.21 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 127.732 | 168.349 | 171.021 | 159.264 | 112.767 | 78.5629 | 61.4608 | 49.7031 | 44.8931 | 40.6176 | 36.8765 | 29.9287
| 23.8 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 138.42 | 181.176 | 190.261 | 181.71 | 140.558 | 100.475 | 80.7007 | 64.6675 | 57.1853 | 52.3753 | 47.5653 | 39.0143
| 29.57 | x | 0 | 0.19331 | 0.29989 | 0.39254 | 0.59847 | 0.79417 | 1.0072 | 1.2098 | 1.4057 | 1.5981 | 1.7974 | 2
|  | y | 155.523 | 197.209 | 202.553 | 194.002 | 149.644 | 109.561 | 88.1829 | 68.943 | 61.4608 | 55.5819 | 51.8409 | 42.2209
0.2 | 3.38 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 53.4474 | 57.6642 | 60.0955 | 51.2484 | 41.8074 | 28.2741 | 18.885 | 16.0402 | 12.5955 | 11.5239 | 9.8586 | 8.7912 | 6.5361
| 4.93 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 65.3237 | 70.7323 | 71.9718 | 63.1309 | 52.4982 | 37.1771 | 26.0128 | 21.9742 | 17.9378 | 16.8683 | 14.6091 | 13.5417 | 10.099
| 6.95 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 81.9526 | 92.6972 | 95.1326 | 84.5082 | 68.5332 | 47.2741 | 34.3262 | 27.9124 | 23.8759 | 21.027 | 18.172 | 16.5107 | 13.066
| 9.44 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 99.767 | 109.328 | 110.57 | 98.1638 | 82.7827 | 59.74 | 42.6396 | 37.4155 | 31.0017 | 27.5549 | 24.1122 | 21.8551 | 18.4103
| 12.56 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 119.959 | 130.708 | 130.757 | 115.976 | 96.4404 | 71.0225 | 52.7365 | 45.1351 | 37.5357 | 33.493 | 30.0503 | 28.9808 | 21.9732
| 16.45 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 143.113 | 156.24 | 157.483 | 142.698 | 119.601 | 87.6514 | 64.0169 | 54.0381 | 44.0614 | 40.6188 | 35.9885 | 34.3272 | 26.7237
| 20.21 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 153.21 | 170.485 | 174.706 | 164.073 | 139.787 | 102.497 | 75.2994 | 62.3578 | 50.5955 | 45.9652 | 41.3349 | 39.0798 | 31.4763
| 23.8 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 178.746 | 200.774 | 206.774 | 192.578 | 167.1 | 123.88 | 91.3324 | 74.8258 | 62.4759 | 56.06 | 51.4256 | 47.3891 | 39.1938
| 29.57 | x | 0 | 0.1031 | 0.19728 | 0.29874 | 0.40023 | 0.61003 | 0.79878 | 1.0083 | 1.2073 | 1.4028 | 1.5983 | 1.8008 | 2
|  | y | 187.056 | 212.648 | 221.617 | 212.172 | 188.48 | 139.907 | 103.209 | 86.7 | 71.9769 | 63.7837 | 57.9596 | 53.921 | 43.3505
4. Aspect Ratio and Temperature (2005 S.Lee)
Tunnel information
Scale | 1:20 |  | Fire source | Fire size
Length | 10.4 |  | Heptane | 2.47-12.3
|  |  |  | 2.47 | 3.84 | 5.63 | 8.27 | 9.96 | 12.3
Width | 0.06-0.03
| 0.06 | 0.05 | 0.04 | 0.033 | 0.03
Height | 0.03-0.06
| 0.03 | 0.033 | 0.04 | 0.05 | 0.06
As | Distance | Max.T
0.5 | 1 | 140.176
| 1.9948 | 94.4282
| 2.9922 | 72.1408
| 3.9896 | 57.478
| 5.0078 | 49.2669
| 6.0052 | 42.2287
| 7.0026 | 37.5367
0.667 | 1 | 147.801
| 1.9948 | 105.572
| 2.9922 | 82.1114
| 4.0104 | 65.1026
| 5.0078 | 54.5455
| 6.0052 | 48.0938
| 7.0026 | 43.4018
1 | 1 | 151.906
| 1.9948 | 118.475
| 2.9922 | 97.3607
| 4.0104 | 82.1114
| 5.0078 | 68.6217
| 6.0052 | 60.9971
| 7.0234 | 55.132
1.5 | 1 | 119.648
| 1.9948 | 104.985
| 2.9922 | 89.7361
| 4.0104 | 75.6598
| 4.987 | 68.0352
| 5.9844 | 60.9971
| 7.0026 | 55.132
2 | 1 | 107.918
| 2.0156 | 99.1202
| 2.9922 | 86.8035
| 4.0104 | 79.1789
| 5.0078 | 72.7273
| 6.0052 | 66.2757
| 7.0026 | 60.9971
5. Temperature on multiple point extraction (2017 Fengzhu Mei)
Tunnel information
Scale | 1:20 |  | Fire source | Fire size
Length | 8 |  | Propane | 1.5-4.5 [kW]
Width | 0.34 |  |  | 1.5 | 3 | 4.5
Height | 0.44
H | 1.5 kW | 0.29983 | 0.32011 | 0.33994 | 0.36023 | 0.36991 | 0.3796 | 0.3902 | 0.40035 | 0.41049 | 0.42063 | 0.43032
Temp |  | 17.8491 | 18.3396 | 18.8302 | 21.283 | 23.2453 | 31.5849 | 41.3962 | 43.3585 | 45.8113 | 49.7358 | 51.2075
H | 3kW | 0.29983 | 0.32011 | 0.33994 | 0.36023 | 0.36991 | 0.3796 | 0.3902 | 0.40035 | 0.41049 | 0.42063 | 0.43032
Temp |  | 20.7925 | 20.7925 | 22.2642 | 27.1698 | 41.3962 | 55.6226 | 72.3019 | 75.2453 | 78.6792 | 83.5849 | 87.0189
H | 4.5 kW | 0.29983 | 0.32011 | 0.33994 | 0.36023 | 0.36991 | 0.3796 | 0.3902 | 0.40035 | 0.41049 | 0.42063 | 0.43032
Temp |  | 22.7547 | 23.7358 | 25.2075 | 44.3396 | 80.6415 | 96.8302 | 114 | 118.906 | 119.887 | 127.245 | 131.17
6. Temperature on ceiling above vertical shafts (2019 Shengzhong Zhao)
Tunnel information
Scale | 1:8 |  | Fire source | Fire size
Length | 20 |  | Kerosene | 30.3-79.4 [kW]
Width | 2
Height | 1
Venilation speed |  | 0-1
Number of shaft |  | 0-3
Location | HRR | Ventilation speed | 0.2426 | 1.2723 | 2.1065 | 2.9314 | 3.7261 | 4.7409 | 5.7489 | 6.7568 | 7.8232 | 8.8473 | 9.7737 | 10.7886 | 11.8757 | 12.926 | 13.934 | 14.9281 | 15.8707 | 16.9279 | 17.9267 | 18.9254
Temp. | 71.9 | 0 | 149.782 | 165.066 | 310.262 | 189.52 | 166.594 | 152.838 | 143.668 | 134.498 | 125.328 | 105.459 | 111.572 | 97.8166 | 74.8908 | 76.4192 | 67.2489 | 67.2489 | 62.6638 | 59.607 | 56.5502 | 53.4934
| 48.7 | 0.5 | 119.214 | 129.913 | 152.838 | 178.821 | 119.214 | 85.5895 | 90.1747 | 85.5895 | 84.0611 | 81.0044 | 79.476 | 74.8908 | 38.2096 | 62.6638 | 61.1354 | 59.607 | 58.0786 | 56.5502 | 55.0218 | 51.9651
| 49 | 0.75 | 93.2314 | 106.987 | 131.441 | 152.838 | 122.271 | 81.0044 | 79.476 | 76.4192 | 74.8908 | 71.8341 | 71.8341 | 70.3057 | 41.2664 | 56.5502 | 56.5502 | 51.9651 | 51.9651 | 51.9651 | 50.4367 | 48.9083
| 59 | 1 | 19.869 | 73.3624 | 129.913 | 184.934 | 126.856 | 84.0611 | 76.4192 | 71.8341 | 73.3624 | 68.7773 | 67.2489 | 64.1921 | 47.3799 | 59.607 | 58.0786 | 55.0218 | 53.4934 | 53.4934 | 53.4934 | 50.4367
Location | HRR | Ventilation speed | 0.2426 | 1.2723 | 2.1065 | 2.9314 | 3.7261 | 4.7409 | 5.7489 | 6.7568 | 7.8232 | 8.8473 | 9.7737 | 10.7886 | 11.8757 | 12.926 | 13.934 | 14.9281 | 15.8707 | 16.9279 | 17.9267 | 18.9254
Temp. | 53.4 | 0 | 122.734 | 129.369 | 341.706 | 179.136 | 145.958 | 131.028 | 119.416 | 87.8972 | 86.2383 | 81.2617 | 77.9439 | 74.6262 | 63.014 | 56.3785 | 58.0374 | 54.7196 | 44.7664 | 41.4486 | 36.472 | 35.26
| 46.6 | 0.5 | 104.486 | 114.439 | 150.935 | 167.523 | 129.369 | 87.8972 | 84.5794 | 56.3785 | 69.6495 | 69.6495 | 69.6495 | 41.4486 | 49.743 | 54.7196 | 51.4019 | 39.7897 | 46.4252 | 48.0841 | 47.851 | 45.96
| 50.3 | 0.75 | 121.075 | 134.346 | 169.182 | 192.407 | 126.051 | 97.8505 | 99.5093 | 54.7196 | 76.285 | 76.285 | 74.6262 | 72.9673 | 44.7664 | 54.7196 | 59.6963 | 56.3785 | 58.0374 | 43.1075 | 51.4019 | 51.4019
| 54.9 | 1 | 36.472 | 56.3785 | 149.276 | 159.229 | 121.075 | 89.5561 | 81.2617 | 66.3318 | 71.3084 | 71.3084 | 69.6495 | 53.0607 | 63.014 | 63.014 | 59.6963 | 59.6963 | 46.4252 | 49.743 | 54.7196 | 50.216
Location | HRR | No.shaft | 0.2426 | 1.2723 | 2.1065 | 2.9314 | 3.7261 | 4.7409 | 5.7489 | 6.7568 | 7.8232 | 8.8473 | 9.7737 | 10.7886 | 11.8757 | 12.926 | 13.934 | 14.9281 | 15.8707 | 16.9279 | 17.9267 | 18.9254
Temp. | 53.4 | 3 | 108.5 | 117.25 | 341.25 | 166.25 | 131.25 | 115.5 | 101.5 | 70 | 66.5 | 64.75 | 59.5 | 56 | 43.75 | 38.5 | 40.25 | 33.25 | 33.25 | 26.25 | 24.5 | 15.75
| 71.9 | 1 | 147 | 162.75 | 308 | 185.5 | 164.5 | 152.25 | 141.75 | 133 | 120.75 | 106.75 | 108.5 | 94.5 | 73.5 | 73.5 | 64.75 | 64.75 | 59.5 | 57.75 | 52.5 | 49
| 79.4 | x | 140 | 171.5 | 287 | 189 | 161 | 152.25 | 143.5 | 133 | 120.75 | 105 | 108.5 | 101.5 | 96.25 | 91 | 94.5 | 82.25 | 78.75 | 73.5 | 70 | 66.5
7. Max. Temperature on transverse ventilation with tilt (2018 Long-Xing Yu)
Tunnel information
Scale | Real scale |  | Fire source | Fire size
Length | 2800 |  | Ethanol | 1000-4000
Width | 9
Height | 4
Venilation speed |  | 4
Distance | -25.0435 | -15.3043 | -4.8696 | 0 | 5.2174 | 14.6087 | 44.5217
Temperature | 17.6471 | 40.3922 | 55.6863 | 85.098 | 59.6078 | 43.1373 | 33.7255
Distance | -25.0435 | -15.3043 | -4.8696 | 0 | 5.2174 | 14.9565 | 45.2174
Temperature | 29.8039 | 52.9412 | 68.2353 | 76.0784 | 67.8431 | 55.2941 | 42.3529
Distance | -24.6957 | -14.9565 | -4.8696 | 0 | 5.2174 | 14.6087 | 44.8696 | 74.7826 | 104.696
Temperature | 27.8431 | 50.1961 | 63.9216 | 72.1569 | 64.7059 | 52.9412 | 41.5686 | 30.5882 | 29.0196
Distance | -24.6957 | -14.9565 | -4.8696 | 0 | 5.5652 | 14.9565 | 44.8696 | 74.4348 | 104.696
Temperature | 24.7059 | 47.0588 | 74.1176 | 136.471 | 55.6863 | 46.2745 | 36.4706 | 25.4902 | 24.7059
8. Max. Temperature of full scale experiments with shaft (2009 Tong Yan)
Tunnel information
Scale | Real scale |  | Fire source | Fire size
Length | 1770 |  | Diesel oil | 5000
Width | 12.35
Height | 5.75
Venilation speed |  | 4
length | -26.1176 | -15.7647 | -10.1176 | -6.3529 | -3.0588 | 3.0588 | 5.6471 | 11.0588 | 16.2353
Temperature | 46.551 | 59.6095 | 62.1909 | 98.9371 | 81.0195 | 72.5163 | 65.2278 | 45.7918 | 63.4056
length | -120 | -100.471 | -85.1765 | -74.1176 | -65.4118 | -54.3529 | -44.9412 | -35.2941 | -15.2941 | -5.1765 | 4.7059 | 15.0588 | 35.0588 | 54.8235
Temperature | 29.2408 | 34.4035 | 32.885 | 36.2256 | 41.9957 | 43.6659 | 46.7028 | 45.3362 | 55.8134 | 83.9046 | 87.5488 | 76.7679 | 58.5466 | 48.9805
length | -115.294 | -95.7647 | -75.0588 | -64.9412 | -55.2941 | -45.4118 | -25.1765 | -14.8235 | -4.9412 | 4.4706 | 14.8235 | 24.2353 | 39.7647 | 60
Temperature | 28.026 | 30.1518 | 36.9848 | 37.744 | 45.9436 | 48.8286 | 55.3579 | 70.846 | 92.1041 | 93.9262 | 57.9393 | 57.4837 | 55.0542 | 46.8547
9. Max. Temperature with one opening portal (2014 Miao Cheng)
Tunnel information
Scale | Real scale |  | Fire source | Fire size
Length | 2112 |  | Diesel oil | 1350-3800
Width | 13.2 |  |  | 1350
Height | 7.3 |  |  | 3000
Venilation speed |  | 4 |  | 3800
[13 empty] | Q | Temp.
[13 empty] | 1350 | 78.6
[13 empty] | 1350 | 87.8
[13 empty] | 3000 | 137.4
[13 empty] | 3000 | 152
[13 empty] | 3800 | 155.9
[13 empty] | 3800 | 166.7
10. Max. temperature in curved sidewall (2020Rongliang Pan)
Tunnel information
Scale | 1:4 |  | Fire source | Fire size
Length | 20 |  | Diesel oil | 9.61-64.5 | [kW]
Width | 1.5
Height | 1.5
Distance | 0 | 15 | 30 | 45 | 60
Temp | 512.501 | 429.252 | 420.997 | 417.263 | 442.008
Distance | 0 | 15 | 30 | 45 | 60
Temp | 692.496 | 594.254 | 551.506 | 547.75 | 641.51
Distance | 0 | 15 | 30 | 45 | 60
Temp | 953.499 | 862.765 | 778.008 | 774.26 | 982.014
11. Max. temperature in closed utility tunnel (2019 Hao-nan Lui)
Tunnel information
Scale | unknown small scale |  | Fire source | Fire size
Length | 20 |  | Diesel oil | 8.94-59.64
Width | 1.5 |  |  | 8.94
Height | 1.5 |  |  | 26.84
59.64
size of oil pan | 17 | 27 | 35
Experiment value | 230 | 370 | 590
Li's value | 125 | 256 | 435
Corrected value | 218 | 390 | 620
12. Max. temperature in branced tunnel (2019 Youbo Huang)
Tunnel information
Scale | 1:20 |  | Fire source | Fire size
Length | 30.66 |  | LPG | 1.72-6.04 | [kW]
Width | 0.675 |  |  | 1.72
Height | 0.355 |  |  | 2.59
Veniltation speed |  |  |  | 3.45
0.23-1 [m/s] |  |  |  | 4.31
5.18
6.04
HRR
ventilation speed | 1.72 | 0.24901 | 0.33829 | 0.39956 | 0.53786 | 0.61838
Temperature |  | 150.474 | 141.263 | 128.368 | 111.421 | 109.579
ventilation speed | 2.59 | 0.34179 | 0.39781 | 0.53786 | 0.62188 | 0.73917
Temperature |  | 174.421 | 164.105 | 146.421 | 139.789 | 122.842
ventilation speed | 3.45 | 0.40131 | 0.53786 | 0.61838 | 0.73917 | 0.82845
Temperature |  | 201.316 | 174.421 | 164.105 | 143.105 | 123.947
ventilation speed | 4.31 | 0.53961 | 0.61838 | 0.73742 | 0.8267 | 0.91597
Temperature |  | 203.895 | 191.368 | 169.263 | 147.158 | 117.684
ventilation speed | 5.18 | 0.53786 | 0.61838 | 0.73742 | 0.82495 | 0.91772
Temperature |  | 235.579 | 210.158 | 189.158 | 171.842 | 153.789
ventilation speed | 6.04 | 0.61663 | 0.73392 | 0.82845 | 0.91948 | 0.9965
Temperature |  | 226 | 207.579 | 195.053 | 176.632 | 148.263

## Database_ceiling Temp.
[11 empty] | Q | HRR
[11 empty] | V | Ventilation speed
[11 empty] | H | Tunnel height
Scale factor | Q [kW] | L [m] | W [m] | H [m] | V [m/s] | Fire source | Fire location | Max. Ceiling Temp. [oC] | Ref | Remarks | C | Center
1:10 | 64 | 16.5 | 1.3 | 0.3 | 0 | LPG | C | 1094.7 | [1]
1:10 | 64 | 16.5 | 1.3 | 0.35 | 0 | LPG | C | 1112.15 | [1]
1:10 | 64 | 16.5 | 1.3 | 0.4 | 0 | LPG | C | 1077.26 | [1]
1:10 | 104 | 16.5 | 1.3 | 0.3 | 0 | LPG | C | 1162.31 | [1]
1:10 | 104 | 16.5 | 1.3 | 0.35 | 0 | LPG | C | 1131.8 | [1]
1:10 | 104 | 16.5 | 1.3 | 0.4 | 0 | LPG | C | 1109.98 | [1]
1:10 | 64 | 16.5 | 1.3 | 0.3 | 0.3 | LPG | C | 940.299 | [1]
1:10 | 64 | 16.5 | 1.3 | 0.3 | 0.6 | LPG | C | 814.925 | [1]
1:10 | 64 | 16.5 | 1.3 | 0.3 | 0.9 | LPG | C | 696.517 | [1]
1:10 | 64 | 16.5 | 1.3 | 0.3 | 1.2 | LPG | C | 480.597 | [1]
1:10 | 64 | 16.5 | 1.3 | 0.3 | 1.5 | LPG | C | 355.224 | [1]
1:10 | 112 | 16.5 | 1.3 | 0.3 | 0.3 | LPG | C | 1057 | [1]
1:10 | 112 | 16.5 | 1.3 | 0.3 | 0.6 | LPG | C | 938 | [1]
1:10 | 112 | 16.5 | 1.3 | 0.3 | 0.9 | LPG | C | 819 | [1]
1:10 | 112 | 16.5 | 1.3 | 0.3 | 1.2 | LPG | C | 602 | [1]
1:10 | 112 | 16.5 | 1.3 | 0.3 | 1.5 | LPG | C | 434 | [1]
1:10 | 144 | 16.5 | 1.3 | 0.3 | 0.3 | LPG | C | 1119.33 | [1]
1:10 | 144 | 16.5 | 1.3 | 0.3 | 0.6 | LPG | C | 1008.31 | [1]
1:10 | 144 | 16.5 | 1.3 | 0.3 | 0.9 | LPG | C | 872.224 | [1]
1:10 | 144 | 16.5 | 1.3 | 0.3 | 1.2 | LPG | C | 678.42 | [1]
1:10 | 144 | 16.5 | 1.3 | 0.3 | 1.5 | LPG | C | 471.654 | [1]
1:23 | 1.1 | 12 | 0.25 | 0.25 | 0.11 | Porous bed burner | C | 143.8 | [2]
1:23 | 1.2 | 12 | 0.25 | 0.25 | 0.05 | Porous bed burner | C | 202.7 | [2]
1:23 | 1.9 | 12 | 0.25 | 0.25 | 0.13 | Porous bed burner | C | 349.1 | [2]
1:23 | 4.3 | 12 | 0.25 | 0.25 | 0.08 | Porous bed burner | C | 463.1 | [2]
1:23 | 4.3 | 12 | 0.25 | 0.25 | 0.7 | Porous bed burner | C | 216.5 | [2]
1:23 | 4.3 | 12 | 0.25 | 0.25 | 0.59 | Porous bed burner | C | 256 | [2]
1:23 | 4.3 | 12 | 0.25 | 0.25 | 0.36 | Porous bed burner | C | 296 | [2]
1:23 | 5.2 | 12 | 0.25 | 0.25 | 0.69 | Porous bed burner | C | 271.2 | [2]
1:23 | 5.2 | 12 | 0.25 | 0.25 | 0.59 | Porous bed burner | C | 313.1 | [2]
1:23 | 5.2 | 12 | 0.25 | 0.25 | 0.34 | Porous bed burner | C | 358.7 | [2]
1:23 | 6 | 12 | 0.25 | 0.25 | 0.72 | Porous bed burner | C | 297.2 | [2]
1:23 | 6 | 12 | 0.25 | 0.25 | 0.66 | Porous bed burner | C | 321.8 | [2]
1:23 | 6 | 12 | 0.25 | 0.25 | 0.58 | Porous bed burner | C | 360.8 | [2]
1:23 | 6 | 12 | 0.25 | 0.25 | 0.48 | Porous bed burner | C | 363.5 | [2]
1:23 | 2 | 12 | 0.25 | 0.393 | 0.33 | Porous bed burner | C | 53.9 | [2] | Horse hoof shape tunnel
1:23 | 2 | 12 | 0.25 | 0.393 | 0.36 | Porous bed burner | C | 49.1 | [2] | Horse hoof shape tunnel
1:23 | 2 | 12 | 0.25 | 0.393 | 0.38 | Porous bed burner | C | 45.8 | [2] | Horse hoof shape tunnel
1:23 | 2.4 | 12 | 0.25 | 0.393 | 0.1 | Porous bed burner | C | 130.9 | [2] | Horse hoof shape tunnel
1:23 | 2.4 | 12 | 0.25 | 0.393 | 0.12 | Porous bed burner | C | 129.8 | [2] | Horse hoof shape tunnel
1:23 | 3.5 | 12 | 0.25 | 0.393 | 0.41 | Porous bed burner | C | 89.4 | [2] | Horse hoof shape tunnel
1:23 | 3.5 | 12 | 0.25 | 0.393 | 0.43 | Porous bed burner | C | 77.7 | [2] | Horse hoof shape tunnel
1:23 | 3.5 | 12 | 0.25 | 0.393 | 0.45 | Porous bed burner | C | 72.8 | [2] | Horse hoof shape tunnel
1:23 | 4.6 | 12 | 0.25 | 0.393 | 0.43 | Porous bed burner | C | 106.8 | [2] | Horse hoof shape tunnel
1:23 | 4.6 | 12 | 0.25 | 0.393 | 0.45 | Porous bed burner | C | 95 | [2] | Horse hoof shape tunnel
1:23 | 4.6 | 12 | 0.25 | 0.393 | 0.49 | Porous bed burner | C | 97.3 | [2] | Horse hoof shape tunnel
1:23 | 4.6 | 12 | 0.25 | 0.393 | 0.53 | Porous bed burner | C | 88.5 | [2] | Horse hoof shape tunnel
1:23 | 5.9 | 12 | 0.25 | 0.393 | 0.09 | Porous bed burner | C | 290.1 | [2] | Horse hoof shape tunnel
1:23 | 5.9 | 12 | 0.25 | 0.393 | 0.13 | Porous bed burner | C | 287.7 | [2] | Horse hoof shape tunnel
1:23 | 7.5 | 12 | 0.25 | 0.393 | 0.11 | Porous bed burner | C | 335.6 | [2] | Horse hoof shape tunnel
1:23 | 7.5 | 12 | 0.25 | 0.393 | 0.2 | Porous bed burner | C | 310 | [2] | Horse hoof shape tunnel
1:23 | 7.5 | 12 | 0.25 | 0.393 | 0.23 | Porous bed burner | C | 330 | [2] | Horse hoof shape tunnel
1:23 | 11.5 | 12 | 0.25 | 0.393 | 0.05 | Porous bed burner | C | 451 | [2] | Horse hoof shape tunnel
1:23 | 14 | 12 | 0.25 | 0.393 | 0.1 | Porous bed burner | C | 492.2 | [2] | Horse hoof shape tunnel
1:23 | 11.5 | 12 | 0.25 | 0.393 | 0.12 | Porous bed burner | C | 437.1 | [2] | Horse hoof shape tunnel
1:6 | 3.38 | 6 | 2 | 0.88 | 0 | Methanol | C | 329.2502 | [3]
1:6 | 4.93 | 6 | 2 | 0.88 | 0 | Methanol | C | 344.1473 | [3]
1:6 | 6.95 | 6 | 2 | 0.88 | 0 | Methanol | C | 370.8583 | [3]
1:6 | 9.44 | 6 | 2 | 0.88 | 0 | Methanol | C | 386.27 | [3]
1:6 | 12.56 | 6 | 2 | 0.88 | 0 | Methanol | C | 395.515 | [3]
1:6 | 16.45 | 6 | 2 | 0.88 | 0 | Methanol | C | 423.767 | [3]
1:6 | 20.21 | 6 | 2 | 0.88 | 0 | Methanol | C | 439.178 | [3]
1:6 | 23.8 | 6 | 2 | 0.88 | 0 | Methanol | C | 456.131 | [3]
1:6 | 29.57 | 6 | 2 | 0.88 | 0 | Methanol | C | 477.705 | [3]
1:6 | 3.38 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 330.7778 | [3]
1:6 | 4.93 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 344.1111 | [3]
1:6 | 6.95 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 364.1111 | [3]
1:6 | 9.44 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 383 | [3]
1:6 | 12.56 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 401.333 | [3]
1:6 | 16.45 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 419.111 | [3]
1:6 | 20.21 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 427.444 | [3]
1:6 | 23.8 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 448.556 | [3]
1:6 | 29.57 | 6 | 2 | 0.88 | 0 | Methanol | 0.75 C | 467.444 | [3]
1:6 | 3.38 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 330.0205 | [3]
1:6 | 4.93 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 341.8356 | [3]
1:6 | 6.95 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 361.8699 | [3]
1:6 | 9.44 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 382.418 | [3]
1:6 | 12.56 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 397.315 | [3]
1:6 | 16.45 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 423 | [3]
1:6 | 20.21 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 436.356 | [3]
1:6 | 23.8 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 459.986 | [3]
1:6 | 29.57 | 6 | 2 | 0.88 | 0 | Methanol | 0.5 C | 473.856 | [3]
1:6 | 3.38 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 327.8928 | [3]
1:6 | 4.93 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 349.0054 | [3]
1:6 | 6.95 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 362.2761 | [3]
1:6 | 9.44 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 387.611 | [3]
1:6 | 12.56 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 391.231 | [3]
1:6 | 16.45 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 417.772 | [3]
1:6 | 20.21 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 432.249 | [3]
1:6 | 23.8 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 455.172 | [3]
1:6 | 29.57 | 6 | 2 | 0.88 | 0 | Methanol | 0.4 C | 478.697 | [3]
1:6 | 3.38 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 333.3919 | [3]
1:6 | 4.93 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 343.0119 | [3]
1:6 | 6.95 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 363.8551 | [3]
1:6 | 9.44 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 385.767 | [3]
1:6 | 12.56 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 404.473 | [3]
1:6 | 16.45 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 430.66 | [3]
1:6 | 20.21 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 444.021 | [3]
1:6 | 23.8 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 463.261 | [3]
1:6 | 29.57 | 6 | 2 | 0.88 | 0 | Methanol | 0.3 C | 475.553 | [3]
1:6 | 3.38 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 333.0955 | [3]
1:6 | 4.93 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 344.9718 | [3]
1:6 | 6.95 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 368.1326 | [3]
1:6 | 9.44 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 383.57 | [3]
1:6 | 12.56 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 403.757 | [3]
1:6 | 16.45 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 430.483 | [3]
1:6 | 20.21 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 447.706 | [3]
1:6 | 23.8 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 479.774 | [3]
1:6 | 29.57 | 6 | 2 | 0.88 | 0 | Methanol | 0.2 C | 494.617 | [3]
1:20 | 8.27 | 10.4 | 0.06 | 0.03 | 0 | Heptance | C | 140.176 | [4]
1:20 | 8.27 | 10.4 | 0.05 | 0.333 | 0 | Heptance | C | 147.801 | [4]
1:20 | 8.27 | 10.4 | 0.04 | 0.04 | 0 | Heptance | C | 151.906 | [4]
1:20 | 8.27 | 10.4 | 0.333 | 0.05 | 0 | Heptance | C | 119.648 | [4]
1:20 | 8.27 | 10.4 | 0.03 | 0.06 | 0 | Heptance | C | 107.918 | [4]
1:20 | 1.5 | 8 | 0.34 | 0.44 | without vent | Propane | C | 51.6 | [5]
1:20 | 3 | 8 | 0.34 | 0.44 | without vent | Propane | C | 86.4 | [5]
1:20 | 4.5 | 8 | 0.34 | 0.44 | without vent | Propane | C | 130.8 | [5]
1:8 | 71.9 | 20 | 2 | 1 | 0 | Kerosene | C | 310.262 | [6] | One exhaust shaft
1:8 | 48.7 | 20 | 2 | 1 | 0.5 | Kerosene | C | 178.821 | [6] | One exhaust shaft
1:8 | 49 | 20 | 2 | 1 | 0.75 | Kerosene | C | 152.838 | [6] | One exhaust shaft
1:8 | 59 | 20 | 2 | 1 | 1 | Kerosene | C | 184.934 | [6] | One exhaust shaft
1:8 | 53.4 | 20 | 2 | 1 | 0 | Kerosene | C | 341.706 | [6] | Three exhaust shaft
1:8 | 46.6 | 20 | 2 | 1 | 0.5 | Kerosene | C | 167.523 | [6] | Three exhaust shaft
1:8 | 50.3 | 20 | 2 | 1 | 0.75 | Kerosene | C | 192.407 | [6] | Three exhaust shaft
1:8 | 54.9 | 20 | 2 | 1 | 1 | Kerosene | C | 149.276 | [6] | Three exhaust shaft
1:8 | 53.4 | 20 | 2 | 1 | 0 | Kerosene | C | 341.25 | [6] | No exhaust shaft
1:8 | 71.9 | 20 | 2 | 1 | 0 | Kerosene | C | 308 | [6] | No exhaust shaft
1:8 | 79.4 | 20 | 2 | 1 | 0 | Kerosene | C | 287 | [6] | No exhaust shaft
1:4 | 9.61 | 20 | 1.5 | 1.5 | Without vent | Oil pan | C | 239.501 | [10] | Round shape tunnel
1:4 | 28.8 | 20 | 1.5 | 1.5 | Without vent | Oil pan | C | 419.496 | [10] | Round shape tunnel
1:4 | 64.5 | 20 | 1.5 | 1.5 | Without vent | Oil pan | C | 680.499 | [10] | Round shape tunnel
- | 8.94 | 20 | 1.5 | 1.5 | Without vent | Diesel oil | C | 225 | [11] | Round shape tunnel
- | 26.84 | 20 | 1.5 | 1.5 | Without vent | Diesel oil | C | 380 | [11] | Round shape tunnel
- | 59.64 | 20 | 1.5 | 1.5 | Without vent | Diesel oil | C | 595 | [11] | Round shape tunnel
1:20 | 1.72 | 30.66 | 0.675 | 0.355 | 0.24901 | LPG | C | 150.474 | [12]
1:20 | 1.72 | 30.66 | 0.675 | 0.355 | 0.33829 | LPG | C | 141.263 | [12]
1:20 | 1.72 | 30.66 | 0.675 | 0.355 | 0.39956 | LPG | C | 128.368 | [12]
1:20 | 1.72 | 30.66 | 0.675 | 0.355 | 0.53786 | LPG | C | 111.421 | [12]
1:20 | 1.72 | 30.66 | 0.675 | 0.355 | 0.61838 | LPG | C | 109.579 | [12]
1:20 | 2.59 | 30.66 | 0.675 | 0.355 | 0.34179 | LPG | C | 174.421 | [12]
1:20 | 2.59 | 30.66 | 0.675 | 0.355 | 0.39781 | LPG | C | 164.105 | [12]
1:20 | 2.59 | 30.66 | 0.675 | 0.355 | 0.53786 | LPG | C | 146.421 | [12]
1:20 | 2.59 | 30.66 | 0.675 | 0.355 | 0.62188 | LPG | C | 139.789 | [12]
1:20 | 2.59 | 30.66 | 0.675 | 0.355 | 0.73917 | LPG | C | 122.842 | [12]
1:20 | 3.45 | 30.66 | 0.675 | 0.355 | 0.40131 | LPG | C | 201.316 | [12]
1:20 | 3.45 | 30.66 | 0.675 | 0.355 | 0.53786 | LPG | C | 174.421 | [12]
1:20 | 3.45 | 30.66 | 0.675 | 0.355 | 0.61838 | LPG | C | 164.105 | [12]
1:20 | 3.45 | 30.66 | 0.675 | 0.355 | 0.73917 | LPG | C | 143.105 | [12]
1:20 | 3.45 | 30.66 | 0.675 | 0.355 | 0.82845 | LPG | C | 123.947 | [12]
1:20 | 4.31 | 30.66 | 0.675 | 0.355 | 0.53961 | LPG | C | 203.895 | [12]
1:20 | 4.31 | 30.66 | 0.675 | 0.355 | 0.61838 | LPG | C | 191.368 | [12]
1:20 | 4.31 | 30.66 | 0.675 | 0.355 | 0.73742 | LPG | C | 169.263 | [12]
1:20 | 4.31 | 30.66 | 0.675 | 0.355 | 0.8267 | LPG | C | 147.158 | [12]
1:20 | 4.31 | 30.66 | 0.675 | 0.355 | 0.91597 | LPG | C | 117.684 | [12]
1:20 | 5.18 | 30.66 | 0.675 | 0.355 | 0.53786 | LPG | C | 235.579 | [12]
1:20 | 5.18 | 30.66 | 0.675 | 0.355 | 0.61838 | LPG | C | 210.158 | [12]
1:20 | 5.18 | 30.66 | 0.675 | 0.355 | 0.73742 | LPG | C | 189.158 | [12]
1:20 | 5.18 | 30.66 | 0.675 | 0.355 | 0.82495 | LPG | C | 171.842 | [12]
1:20 | 5.18 | 30.66 | 0.675 | 0.355 | 0.91772 | LPG | C | 153.789 | [12]
1:20 | 6.04 | 30.66 | 0.675 | 0.355 | 0.61663 | LPG | C | 226 | [12]
1:20 | 6.04 | 30.66 | 0.675 | 0.355 | 0.73392 | LPG | C | 207.579 | [12]
1:20 | 6.04 | 30.66 | 0.675 | 0.355 | 0.82845 | LPG | C | 195.053 | [12]
1:20 | 6.04 | 30.66 | 0.675 | 0.355 | 0.91948 | LPG | C | 176.632 | [12]
1:20 | 6.04 | 30.66 | 0.675 | 0.355 | 0.9965 | LPG | C | 148.263 | [12]
Real | 1000 | 2800 | 9 | 4 | 4 | Ethanol | C | 85.098 | [7] | at 300 s after fires
Real | 1000 | 2800 | 9 | 4 | 4 | Ethanol | C | 76.0784 | [7] | at 300 s after fires
Real | 1000 | 2800 | 9 | 4 | 4 | Ethanol | C | 72.1569 | [7] | at 300 s after fires
Real | 1000 | 2800 | 9 | 4 | 4 | Ethanol | C | 136.471 | [7] | at 300 s after fires
Real | 5000 | 1770 | 12.35 | 5.75 | NVS | Diesel | C | 98.9371 | [8]
Real | 5000 | 1770 | 12.35 | 5.75 | NVS | Diesel | C | 87.5488 | [8]
Real | 5000 | 1770 | 12.35 | 5.75 | NVS | Diesel | C | 93.9262 | [8]
Real | 1350 | 2112 | 13.2 | 7.3 | without vent | Diesel | C | 78.6 | [9] | Horse hoof shape tunnel
Real | 1350 | 2112 | 13.2 | 7.3 | without vent | Diesel | C | 87.8 | [9] | Horse hoof shape tunnel
Real | 3000 | 2112 | 13.2 | 7.3 | without vent | Diesel | C | 137.4 | [9] | Horse hoof shape tunnel
Real | 3000 | 2112 | 13.2 | 7.3 | without vent | Diesel | C | 152 | [9] | Horse hoof shape tunnel
Real | 3800 | 2112 | 13.2 | 7.3 | without vent | Diesel | C | 155.9 | [9] | Horse hoof shape tunnel
Real | 3800 | 2112 | 13.2 | 7.3 | without vent | Diesel | C | 166.7 | [9] | Horse hoof shape tunnel

## reference
Ref. No. | Title
1 | Experimental study on the maximum temperature and flame extension length driven by strong plume in a longitudinal ventilated tunnel (2019 Longfei Chen)
2 | The maximum temperature of buoyancy-driven smoke flow beneath the ceiling (2011 Ying Zhen Li )
3 | Experimental study on transverse smoke temperature distribution in road tunnel fire (2013 C. G. Fan et al. )
4 | An Experimental Study of the Effect of the Aspect Ratio on the Critical Velocity in Longitudinal Ventilation Tunnel Fires (2005 S.Lee)
5 | Evolution characteristics of fire smoke layer thickness in a mechanical ventilation tunnel with multiple point extraction (2017 Fengzhu Mei)
6 | A theoretical and experimental study on the buoyancy-driven smoke flow in a tunnel with vertical shafts (2019 Shengzhong Zhao)
7 | Studies on buoyancy driven two-directional smoke flow layering length with combination of point extraction and longitudinal ventilation in tunnel fires (2013 L.F.Chen)
8 | Full-scale experimental study on smoke flow in natural ventilation road tunnel fires with shafts (2009 Tong Yan)
9 | Full-scale experiment and CFD simulation on smoke movement and smoke control in a metro tunnel with one opening portal (2014 Miao Cheng Weng)
10 | Experimental study on the fire shape and maximum temperature beneath ceiling centerline in utility tunnel under the effect of curved sidewall (2020Rongliang Pan et al.)
11 | Effect of cross-wind on near-wall buoyant turbulent diffusion flame length and tilt (2016Fei Tang et al.)
12 | Experimental investigation on maximum gas temperature beneath the ceiling in a branched tunnel fire