## 3.6 Smoke layer thickness
1. Smoke layer thickness in a mechanical ventilation with multiple extraction (2017 Fengzhu Mei)
Tunnel information
Scale | 1:20
Length | 8
Width | 0.34
Height | 0.44
Fire source | Propane gas burner
Fire size [kW] | 1.5 | 3 | 4.5
HRR | 1.5 | 3 | 4.5
Thickness | 0.05 | 0.06 | 0.07 | Integral ratio
| 0.052166 | 0.065096 | 0.072229 | Visual value
| 0.04949 | 0.060191 | 0.069554 | Within-class variance method
2. Smoke layer thickness in middle scale tunnel (2016 Z. H. Gao)
Tunnel information
Scale | 1:20 | [5 empty] | Test No. | Ambient temp. [o] | Pool size [cm] | Experiments condition
Length | 6 | [5 empty] | Case 1 | 16 | 10 x 15 | Without smoke exhaust
Width | 2 | [5 empty] | Case 2 | 15 | 15 x 20 | Without smoke exhaust
Height | 0.9 | [5 empty] | Case 3 | 15 | 10 x 15 | Natural smoke exhaust
Fire source | Heptane | [5 empty] | Case 4 | 17 | 15 x 20 | Natural smoke exhaust
Fire size [kW] | 82 | 128
Smoke layer thickness discriminant way |  |  |  |  | Integral ratio
N=10 | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.24509 | 0.19973 | 0.22041 | 0.225 | 0.22998 | 0.22136 | 0.22016 | 0.21525 | 0.22107 | 0.2306
N =20 | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.22982 | 0.19024 | 0.20473 | 0.20023 | 0.2143 | 0.20568 | 0.20489 | 0.20494 | 0.20539 | 0.20543
N =30 | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.22033 | 0.17002 | 0.18409 | 0.18537 | 0.20481 | 0.18958 | 0.19953 | 0.20122 | 0.1959 | 0.19552
Integral ratio | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.12458 | 0.12957 | 0.14984 | 0.14534 | 0.16519 | 0.1706 | 0.17972 | 0.17563 | 0.17114 | 0.17035
Buoyancy frequency method | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.16585 | 0.15558 | 0.17047 | 0.1701 | 0.19037 | 0.19536 | 0.20613 | 0.21113 | 0.20085 | 0.19553
Visual value | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.16007 | 0.16012 | 0.16965 | 0.18042 | 0.20027 | 0.2098 | 0.21026 | 0.21071 | 0.20002 | 0.20048
N=10 | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.18974 | 0.18497 | 0.20025 | 0.17987 | 0.18497 | 0.19484 | 0.18529 | 0.19516 | 0.20503
N =20 | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.15981 | 0.1649 | 0.16522 | 0.1649 | 0.17 | 0.17 | 0.17032 | 0.17478 | 0.17955
N =30 | Time [s] | 40 | 60 | 80 | 100 | 110 | 130 | 140 | 160
| Thickness [m] | 0.15025 | 0.15025 | 0.15981 | 0.15471 | 0.15949 | 0.15471 | 0.16459 | 0.1649
Integral ratio | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.1251 | 0.12478 | 0.13019 | 0.12478 | 0.13529 | 0.14994 | 0.15025 | 0.14962 | 0.13465
Buoyancy frequency method | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 160
| Thickness [m] | 0.14994 | 0.14994 | 0.15535 | 0.16968 | 0.19038 | 0.19006 | 0.19006 | 0.17
Visual value | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.14038 | 0.14038 | 0.15057 | 0.14994 | 0.17032 | 0.18974 | 0.19994 | 0.19006 | 0.16968
N=10 | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.21466 | 0.23482 | 0.21494 | 0.2103 | 0.20976 | 0.20486 | 0.20513 | 0.19995 | 0.20486 | 0.2005
N =20 | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.20486 | 0.2242 | 0.2005 | 0.19014 | 0.19478 | 0.19014 | 0.19532 | 0.19014 | 0.19014 | 0.1896
N =30 | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.19505 | 0.20976 | 0.18551 | 0.1847 | 0.1847 | 0.1847 | 0.18497 | 0.18497 | 0.18497 | 0.17979
Integral ratio | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.17026 | 0.16971 | 0.16562 | 0.17543 | 0.16453 | 0.16944 | 0.16998 | 0.17026 | 0.17516 | 0.16018
Buoyancy frequency method | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.1823 | 0.19505 | 0.17516 | 0.17543 | 0.18524 | 0.19587 | 0.20022 | 0.19532 | 0.19532 | 0.19014
Visual value | Time [s] | 40 | 60 | 80 | 100 | 120 | 140 | 150 | 160 | 170 | 180
| Thickness [m] | 0.19 | 0.19941 | 0.18034 | 0.18061 | 0.19042 | 0.20022 | 0.19559 | 0.19995 | 0.18987 | 0.18497
N=10 | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.21988 | 0.21988 | 0.21037 | 0.20003 | 0.20506 | 0.20506 | 0.20478 | 0.21037 | 0.21988
N =20 | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.19025 | 0.20478 | 0.19528 | 0.19053 | 0.195 | 0.19444 | 0.19528 | 0.19025 | 0.20981
N =30 | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.18019 | 0.18522 | 0.17991 | 0.1704 | 0.18438 | 0.18522 | 0.18494 | 0.18522 | 0.18997
Integral ratio | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.16006 | 0.15531 | 0.15503 | 0.16006 | 0.1704 | 0.16453 | 0.16453 | 0.15503 | 0.15503
Buoyancy frequency method | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.18522 | 0.17544 | 0.18997 | 0.19472 | 0.20031 | 0.19528 | 0.18969 | 0.18019 | 0.17516
Visual value | Time [s] | 40 | 60 | 80 | 100 | 110 | 120 | 130 | 140 | 160
| Thickness [m] | 0.18047 | 0.17963 | 0.19025 | 0.20031 | 0.20059 | 0.18997 | 0.19025 | 0.18019 | 0.17991
3. Smoke layer thickness considering vertical shatfs (2019 Shengzhong Zhao)
Tunnel information
Scale
Length
Width
Height
Fire source
Fire size [kW]
Smoke layer thickness discriminant way
u | Q | Smoke layer thickness
0 | 79.4 | 0.70485
0.5 | 51.8 | 0.51101
0.75 | 49.2 | 0.4207
1 | 57.4 | 0.31718
0 | 79.4 | 0.70925
0.5 | 51.8 | 0.53084
0.75 | 49.2 | 0.38106
1 | 57.4 | 0.3304
0 | 33.9 | 0.73568
0.5 | 30.3 | 0.37004
0.75 | 29.9 | 0.30617
1 | 41 | 0.2467
0 | 33.9 | 0.72026
0.5 | 30.3 | 0.38106
0.75 | 29.9 | 0.29075
1 | 41 | 0.29075
4. Smoke layer thickness in full scale immersed tunnel (2018 P. Xu)
Tunnel information
Scale | Real scale
Length | 150
Width | 14.5
Height | 7.1
Fire source | Oil pan
Fire size [kW] | 5000 | 50000
Smoke layer thickness discriminant way |  |  |  |  | measurement
Ventilation speed | HRR | Distance | Height
3 | 25000 | 4.9792 | 0.99867
|  | 9.9475 | 1.5159
|  | 14.7705 | 1.8885
|  | 20.965 | 1.9928
|  | 23.9888 | 1.9932
|  | 35.7805 | 2.0156
|  | 38.8051 | 1.9954
|  | 41.8363 | 1.8099
|  | 44.8605 | 1.8
|  | 56.9633 | 1.6055
|  | 59.6889 | 1.5026
|  | 62.7164 | 1.4101
0 | 25000 | 4.9792 | 2.5069
|  | 9.9475 | 2.8176
|  | 14.7705 | 3.0043
|  | 20.965 | 3.315
|  | 23.9888 | 3.2948
|  | 35.7805 | 3.5239
|  | 38.8051 | 3.5036
|  | 41.8363 | 3.5041
|  | 44.8605 | 3.4942
|  | 56.9633 | 3.4237
|  | 59.6889 | 3.2175
|  | 62.7164 | 3.1146
0 | 50000 | 4.9792 | 3.0234
|  | 9.9475 | 3.4994
|  | 14.7705 | 4.2026
|  | 20.965 | 4.4824
|  | 23.9888 | 4.4932
|  | 35.7805 | 4.4123
|  | 38.8051 | 4.4334
|  | 41.8363 | 4.3202
|  | 44.8605 | 4.207
|  | 56.9633 | 4.0125
|  | 59.6889 | 3.9096
|  | 62.7164 | 3.8171
5. Smoke layer thickness with inclination effect (2012 Jialei Zhang)
Tunnel information
Scale | 1:4
Length | 3.48
Width | 0.4
Height | 0.8
Fire source | Heptane
Fire size [kW]
Smoke layer thickness discriminant way |  |  |  |  | N percent rule; N=10
Tunnel itilt |  | -10 | -5 | 0 | 5 | 10
Degree [0]
Time | 5 | 48.0392 | 100.196 | 150.98 | 201.765 | 249.804 | 297.843 | 348.627 | 398.039 | 448.824 | 496.863 | 547.647
Thickness |  | 33.8898 | 33.1017 | 32.3136 | 33.3644 | 31.3941 | 32.3136 | 32.1822 | 29.6864 | 26.928 | 20.0975 | 5.3856
Time | 10 | 49.4118 | 149.608 | 199.02 | 248.431 | 297.843 | 348.627 | 396.667 | 448.824 | 496.863 | 547.647 | 597.059
Thickness |  | 42.9534 | 38.4873 | 35.072 | 32.7076 | 32.7076 | 33.2331 | 31 | 29.5551 | 19.3093 | 6.6992 | 4.072
Time | 0 | 49.4118 | 150.98 | 201.765 | 248.431 | 297.843 | 347.255 | 398.039 | 446.078 | 498.235 | 546.275 | 598.431
Thickness |  | 41.3771 | 36.1229 | 35.2034 | 34.8093 | 33.7585 | 34.2839 | 33.4958 | 32.7076 | 32.1822 | 29.6864 | 7.6186
Time | -5 | 50.7843 | 100.196 | 148.235 | 201.765 | 249.804 | 297.843 | 351.373 | 398.039 | 447.451 | 498.235 | 547.647
Thickness |  | 38.4873 | 37.9619 | 36.911 | 36.2542 | 36.3856 | 36.911 | 37.3051 | 36.3856 | 36.1229 | 35.4661 | 35.2034
Time | -10 | 52.1569 | 100.196 | 152.353 | 199.02 | 247.059 | 300.588 | 348.627 | 398.039 | 448.824 | 498.235 | 547.647
Thickness |  | 59.7669 | 58.1907 | 57.928 | 57.1398 | 57.4025 | 56.4831 | 56.6144 | 56.2203 | 54.1186 | 49.7839 | 46.5
6. Smoke layer thickness with respect to shaft height and HRR (2020 Lu He)
Tunnel information
Scale | 1:10
Length | 6
Width | 1
Height | 0.7
Fire source | Ethanol
Fire size [kW] |  | 10.66-76.99 |  | [kW]
10.66 | 19.45 | 33.3 | 76.99
Thermal bouyancy frequency value | 0.33911 | 0.41619 | 0.50867 | 0.6474 | 0.81696 | 0.98651 | 1.2486 | 1.526 | 1.8497 | 2.2505 | 2.7437 | 3.2832 | 3.8536 | 4.4701 | 4.948 | 5.3025 | 5.4875 | 5.3487 | 5.0251 | 4.5318 | 3.9615 | 3.3603 | 2.8362 | 2.343 | 1.9268
Height | 0.17869 | 0.19977 | 0.21944 | 0.24052 | 0.25878 | 0.27986 | 0.29953 | 0.3192 | 0.34028 | 0.35995 | 0.38244 | 0.3993 | 0.41897 | 0.44145 | 0.46112 | 0.47939 | 0.50047 | 0.52155 | 0.54262 | 0.56229 | 0.58056 | 0.60023 | 0.61991 | 0.63958 | 0.66206
Thermal bouyancy frequency value | 0.26204 | 0.33911 | 0.4316 | 0.55491 | 0.67823 | 0.8632 | 1.0944 | 1.4027 | 1.788 | 2.3121 | 2.8979 | 3.5761 | 4.3314 | 5.0713 | 5.7033 | 6.0424 | 6.027 | 5.6416 | 5.0251 | 4.2543 | 3.499 | 2.8362 | 2.2505 | 1.7572 | 1.3873
Height | 0.17869 | 0.19977 | 0.21944 | 0.24052 | 0.25878 | 0.27986 | 0.30094 | 0.32061 | 0.34028 | 0.35995 | 0.37962 | 0.3993 | 0.41897 | 0.44005 | 0.45831 | 0.4808 | 0.50047 | 0.52014 | 0.53981 | 0.56229 | 0.57916 | 0.60164 | 0.62131 | 0.64098 | 0.66066
Thermal bouyancy frequency value | 0.2158 | 0.29287 | 0.36994 | 0.49326 | 0.6474 | 0.84778 | 1.1407 | 1.4644 | 1.896 | 2.4354 | 3.1137 | 3.869 | 4.7013 | 5.5029 | 6.0886 | 6.289 | 6.0732 | 5.4721 | 4.6859 | 3.8536 | 3.0829 | 2.42 | 1.8805 | 1.4798 | 1.1252
Height | 0.17869 | 0.19977 | 0.21944 | 0.24052 | 0.25878 | 0.27845 | 0.29953 | 0.3192 | 0.34028 | 0.36136 | 0.38103 | 0.3993 | 0.42178 | 0.44145 | 0.46112 | 0.4808 | 0.50047 | 0.52014 | 0.53981 | 0.5637 | 0.58056 | 0.60023 | 0.62131 | 0.64098 | 0.66066
Thermal bouyancy frequency value | 0.46243 | 0.61657 | 0.80154 | 1.0482 | 1.3564 | 1.7726 | 2.2813 | 2.867 | 3.5915 | 4.3931 | 5.2254 | 5.9962 | 6.4432 | 6.5665 | 6.2428 | 5.5645 | 4.7784 | 3.9152 | 3.1599 | 2.4971 | 1.9422 | 1.5414 | 1.1715 | 0.89403 | 0.69364
Height | 0.17869 | 0.20117 | 0.21944 | 0.24192 | 0.26019 | 0.27845 | 0.29813 | 0.3178 | 0.34028 | 0.36136 | 0.37962 | 0.4007 | 0.42178 | 0.43864 | 0.45972 | 0.4808 | 0.50328 | 0.52155 | 0.54122 | 0.55949 | 0.57916 | 0.60023 | 0.62131 | 0.64098 | 0.66206

## Database_smoke layer
Smoke layer thickness ways
[11 empty] | I | Integral ratio
[11 empty] | N | N-percent rule
Scale factor | Q [kW] | L [m] | W [m] | H [m] | V [m/s] | Fire source | Fire location | Smoke layer thickness. [m] | Ref | Remarks | V | Visual value
1:20 | 1.5 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.05 | [1] | I | W | Within-class variance method
1:20 | 1.5 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.052166 | [1] | V | B | Buoyancy frequency method
1:20 | 1.5 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.04949 | [1] | W | Flame location
1:20 | 3 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.06 | [1] | I | C | Center
1:20 | 3 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.065096 | [1] | V
1:20 | 3 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.060191 | [1] | W | Ventilation system
1:20 | 4.5 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.07 | [1] | I | NVS | Natual Ventilation System
1:20 | 4.5 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.072229 | [1] | V | Without vent
1:20 | 4.5 | 8 | 0.34 | 0.44 | Without vent | Propane | C | 0.069554 | [1] | W
1:20 | 82 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.21576 | [2] | N=10
1:20 | 82 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.20565 | [2] | N=20
1:20 | 82 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.20035 | [2] | N=30
1:20 | 82 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.1758 | [2] | I
1:20 | 82 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.21047 | [2] | B
1:20 | 82 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.21095 | [2] | V
1:20 | 127 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.18514 | [2] | N=10
1:20 | 127 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.16995 | [2] | N=20
1:20 | 127 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.15514 | [2] | N=30
1:20 | 127 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.14995 | [2] | I
1:20 | 127 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.19032 | [2] | B
1:20 | 127 | 6 | 2 | 0.9 | Without vent | Heptane | C | 0.20032 | [2] | V
1:20 | 82 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.20511 | [2] | N=10
1:20 | 82 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.19496 | [2] | N=20
1:20 | 82 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.18481 | [2] | N=30
1:20 | 82 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.16991 | [2] | I
1:20 | 82 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.20004 | [2] | B
1:20 | 82 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.19528 | [2] | V
1:20 | 127 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.20491 | [2] | N=10
1:20 | 127 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.19516 | [2] | N=20
1:20 | 127 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.18509 | [2] | N=30
1:20 | 127 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.16495 | [2] | I
1:20 | 127 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.18996 | [2] | B
1:20 | 127 | 6 | 2 | 0.9 | NVS | Heptane | C | 0.18931 | [2] | V
1:8 | 79.4 | 20 | 2 | 1 | 0 | Kerosene | C | 0.70485 | [3] | N=30
1:8 | 51.8 | 20 | 2 | 1 | 0.5 | Kerosene | C | 0.51101 | [3] | N=30
1:8 | 49.2 | 20 | 2 | 1 | 0.75 | Kerosene | C | 0.4207 | [3] | N=30
1:8 | 57.4 | 20 | 2 | 1 | 1 | Kerosene | C | 0.31718 | [3] | N=30
1:8 | 79.4 | 20 | 2 | 1 | 0 | Kerosene | C | 0.70925 | [3] | N=30
1:8 | 51.8 | 20 | 2 | 1 | 0.5 | Kerosene | C | 0.53084 | [3] | N=30
1:8 | 49.2 | 20 | 2 | 1 | 0.75 | Kerosene | C | 0.38106 | [3] | N=30
1:8 | 57.4 | 20 | 2 | 1 | 1 | Kerosene | C | 0.3304 | [3] | N=30
1:8 | 33.9 | 20 | 2 | 1 | 0 | Kerosene | C | 0.73568 | [3] | N=30
1:8 | 30.3 | 20 | 2 | 1 | 0.5 | Kerosene | C | 0.37004 | [3] | N=30
1:8 | 29.9 | 20 | 2 | 1 | 0.75 | Kerosene | C | 0.30617 | [3] | N=30
1:8 | 41 | 20 | 2 | 1 | 1 | Kerosene | C | 0.2467 | [3] | N=30
1:8 | 33.9 | 20 | 2 | 1 | 0 | Kerosene | C | 0.72026 | [3] | N=30
1:8 | 30.3 | 20 | 2 | 1 | 0.5 | Kerosene | C | 0.38106 | [3] | N=30
1:8 | 29.9 | 20 | 2 | 1 | 0.75 | Kerosene | C | 0.29075 | [3] | N=30
1:8 | 41 | 20 | 2 | 1 | 1 | Kerosene | C | 0.29075 | [3] | N=30
1:4 | - | 3.48 | 0.4 | 0.8 | Without vent | Heptane | C | 0.3389 | [5] | N=10, 5 degree tilt
1:4 | - | 3.48 | 0.4 | 0.8 | Without vent | Heptane | C | 0.42953 | [5] | N=10, 10 degree tilt
1:4 | - | 3.48 | 0.4 | 0.8 | Without vent | Heptane | C | 0.41377 | [5] | N=10, 0 degree tilt
1:4 | - | 3.48 | 0.4 | 0.8 | Without vent | Heptane | C | 0.38487 | [5] | N=10, -5 degree tilt
1:4 | - | 3.48 | 0.4 | 0.8 | Without vent | Heptane | C | 0.59767 | [5] | N=10, -10 degree tilt
1:10 | 10.66 | 6 | 1 | 0.7 | NVS | Ethanol | C | 0.18 | [6] | B
1:10 | 19.45 | 6 | 1 | 0.7 | NVS | Ethanol | C | 0.19 | [6] | B
1:10 | 33.3 | 6 | 1 | 0.7 | NVS | Ethanol | C | 0.2 | [6] | B
1:10 | 76.99 | 6 | 1 | 0.7 | NVS | Ethanol | C | 0.24 | [6] | B
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 0.99867 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.5159 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.8885 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.9928 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.9932 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 2.0156 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.9954 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.8099 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.8 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.6055 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.5026 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 3 | Oil pan | C | 1.4101 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 2.5069 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 2.8176 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.0043 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.315 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.2948 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.5239 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.5036 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.5041 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.4942 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.4237 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.2175 | [4] | V
Real | 25000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.1146 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.0234 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.4994 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.2026 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.4824 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.4932 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.4123 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.4334 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.3202 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.207 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 4.0125 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.9096 | [4] | V
Real | 50000 | 150 | 14.5 | 7.1 | 0 | Oil pan | C | 3.8171 | [4] | V

## reference
Ref. No. | Title
1 | Evolution characteristics of fire smoke layer thickness in a mechanical ventilation tunnel with multiple point extraction (2017 Fengzhu Mei)
2 | Determination of smoke layer interface height of medium scale tunnel fire scenarios (2016 Z.H.Gao)
3 | A theoretical and experimental study on the buoyancy-driven smoke flow in a tunnel with vertical shafts (2019 Shengzhong Zhao)
4 | Full-scale immersed tunnel fire experimental research on smoke flow patterns(2018 P.Xu)
5 | The inclination effect on CO generation and smoke movement in an inclined tunnel fire (2012 Jialei Zhang)
6 | Full-scale experimental study on smoke flow in natural ventilation road tunnel fires with shafts (2009 Tong Yan)