## 3.5 Back-layering
Lb-Back-layering length and other paramenter (2010-Ingason)
From the table
| Test No. | Qmax (kW) | u (m/s) | Lb (m) | T2,max | T1,max
| 1 | 135.3 | 0.54 | 0.15 | 88.9 | 22.5
| 2 | 151.8 | 0.87 | 0 | 77.2 | 19.8
| 3 | 254.7 | 0.45 | 0.205 | 155.2 | 21.7
| 4 | 320.8 | 0.46 | NA | 175.7 | 22.8
| 5 | 145.8 | 0.56 | 0.205 | 108.7 | 22.6
| 6 | 117.9 | 0.45 | 0.7 | 166.1 | 23.4
| 7 | 141.3 | 0.38 | 2.2 | 425.6 | 157.7
| 8 | 142.8 | 0.54 | NA | 155.3 | 23.7
| 9 | 305.2 | 0.76 | NA | 167.2 | 25.3
| 10 | 103.7 | 0.54 | 0 | 60.1 | 22.9
| 11 | 106.7 | 0.86 | 0 | 46.4 | 22.2
| 12 | 102.2 | 0.33 | 1.04 | 116.8 | 24.7
Lb*-Dimensionless back-layering length and V* Dimensionless critical velocity (2010-Ingason)
wood crib A | V* | 0.2741 | 0.3209 | 0.3195 | 0.3264 | 0.3852 | 0.4025 | 0.6183
| Lb* | 7.5875 | 2.7429 | 1.152 | 1.1519 | 0.9662 | 1.1505 | 0.4791
wood crib B | V* | 0.2926 | 0.4712 | 0.7502
| Lb* | 5.5274 | 0.4817 | 0.4767
V - Longitudinal ventilation velocity and Lb backlayering length (2010 Li)
1.8 kW | Lb | 0.2503 | 0.3498 | 0.4493 | 0.6 | 0.7999
| V | 0.4646 | 0.4453 | 0.4291 | 0.4123 | 0.3953
3.2 kW | Lb | 0.1502 | 0.2993 | 0.4502 | 0.65 | 0.8001
| V | 0.5474 | 0.5255 | 0.5022 | 0.475 | 0.4504
4.8 kW | Lb | 0.2 | 0.3998 | 0.6501 | 0.8002
| V | 0.5844 | 0.5444 | 0.519 | 0.5001
6.7 kW | Lb | 0.2498 | 0.3501 | 0.5499 | 0.6999 | 0.8002
| V | 0.6206 | 0.6038 | 0.5718 | 0.5512 | 0.5393
9.2 kW | Lb | 0.2503 | 0.4003 | 0.7
| V | 0.6334 | 0.6118 | 0.5644
12.7 kW | Lb | 0.3514 | 0.6505 | 0.85
| V | 0.6179 | 0.5678 | 0.5451
16.5 kW | Lb | 0.3 | 0.5503 | 0.7004 | 0.9005
| V | 0.6221 | 0.5864 | 0.5646 | 0.54
V** - Dimensionless confinement velocity and L* Dimensionless backlayering length (2010 Li)
1.8 kW | L* | 0.9973 | 1.3978 | 1.7982 | 2.4016
| V** | 0.9281 | 0.8908 | 0.8582 | 0.8256
3.2 kW | L* | 0.597 | 1.7982 | 1.1948 | 2.596 | 3.1995
| V** | 0.9615 | 0.8818 | 0.922 | 0.834 | 0.79
4.8 kW | L* | 0.7973 | 1.5981 | 2.5989 | 3.1995
| V** | 0.928 | 0.865 | 0.8241 | 0.7938
6.7 kW | L* | 0.9973 | 1.395 | 2.1957 | 2.7991 | 3.1994
| V** | 0.9334 | 0.9076 | 0.8606 | 0.8295 | 0.8113
9.2 kW | L* | 0.9973 | 1.5979 | 2.5989 | 2.799
| V** | 0.9456 | 0.9137 | 0.8363 | 0.8409
12.7 kW | L* | 0.1966 | 1.3977 | 2.596 | 3.3967
| V** | 0.9919 | 0.9228 | 0.8484 | 0.8143
16.5 kW | L* | 0 | 1.1976 | 2.1985 | 2.799 | 3.5997 | 2.5989
| V** | 1.0002 | 0.9289 | 0.8765 | 0.8447 | 0.8068 | 0.834
V** - Dimensionless confinement velocity and L* Dimensionless backlayering length (2010 Li)
Tunnel A | L* | 0.1917 | 0.1967 | 0.595 | 0.7941 | 0.7991 | 0.9883 | 0.9832 | 0.9982 | 1.2023 | 1.1924 | 1.3965 | 1.3965 | 1.4015 | 1.5957 | 1.6056 | 1.6006 | 1.6006 | 1.7997 | 1.7997 | 2.1981 | 2.1981 | 2.3972 | 2.6014 | 2.6014 | 2.8005 | 2.9996 | 3.0046 | 3.2038 | 3.2038 | 3.3979 | 4.4036 | 4.8069
| V** | 0.9998 | 0.9922 | 0.9615 | 0.9294 | 0.9554 | 0.9577 | 0.9301 | 0.9416 | 0.9224 | 0.9301 | 0.924 | 0.9087 | 0.8911 | 0.9148 | 0.9118 | 0.8857 | 0.8643 | 0.8819 | 0.8582 | 0.8766 | 0.8612 | 0.8222 | 0.8336 | 0.8237 | 0.8291 | 0.8475 | 0.8191 | 0.8115 | 0.7908 | 0.8153 | 0.777 | 0.7479
Tunnel B | L* | 0.7591 | 0.7591 | 0.8837 | 1.0082 | 1.0082 | 1.0132 | 1.2671 | 1.516 | 1.521 | 1.7749 | 1.7749 | 2.0338 | 2.0288 | 2.2877 | 2.5415 | 2.5415 | 2.7955 | 2.7955 | 3.0493 | 3.0493 | 3.3033 | 3.3033 | 3.5573 | 3.5573 | 3.8112 | 3.8161 | 4.0651 | 4.0701 | 4.0701 | 4.324 | 4.324 | 4.324 | 4.8317 | 4.8317 | 5.0857 | 5.3496 | 5.484 | 5.5985 | 5.5985 | 5.5985 | 5.8524 | 6.1063 | 6.1063 | 6.1661
| V** | 0.9615 | 0.9409 | 0.9455 | 0.9569 | 0.9485 | 0.9278 | 0.9363 | 0.924 | 0.9064 | 0.9079 | 0.8919 | 0.9079 | 0.8789 | 0.8972 | 0.8766 | 0.8658 | 0.8544 | 0.8413 | 0.8735 | 0.8298 | 0.8567 | 0.8444 | 0.8436 | 0.8276 | 0.8161 | 0.8069 | 0.8061 | 0.7939 | 0.7832 | 0.8329 | 0.8153 | 0.8115 | 0.7854 | 0.7747 | 0.7786 | 0.7717 | 0.7656 | 0.7992 | 0.7471 | 0.741 | 0.7372 | 0.7365 | 0.7426 | 0.7441
Comparison of predicted backlayering length with data from the Yuanjiang tunnel tests. (2010 Li)
Heat release rate (MW) | Ventilation velocity (m/s) | Tunnel height (m) | Pool size (m2) | Height of fire source above floor (m) | Backlayering length (m) | Predicted backlayering length using Eq. (31) (m)
1.8 | 1.0–1.1 | 7.2 | 1 | 1.7 | 100 | 63–76
1.8 | 0.6–0.7 | 7.2 | 1 | 0.2 | 140 | 128–150
3.2 | 0.5–0.6 | 7.2 | 2 | 0.2 | 200 | 177–204
3.2 | 0.9–1.0 | 7.2 | 2 | 0.2 | 120 | 104–119
Backlayering length with different tunnel widths and heights. (Fan 2016)
Test | Fuel | uo (m/s) | H (m) | W (m) | A (m2) | Backlayering length (m)
2 | Heptane | 0.67 | 0.25 | 0.45 | 0.11 | 0–0.25
3 | Heptane | 0.67 | 0.25 | 0.6 | 0.15 | 0.5–0.75
4 | Heptane | 0.67 | 0.4 | 0.3 | 0.12 | 0.5–0.75
5 | Heptane | 0.67 | 0.4 | 0.45 | 0.18 | 2.5–2.75
6 | Heptane | 0.5 | 0.4 | 0.6 | 0.24 | >3.75
Lb - Smoke back-layering length with H - shaft heights. (Guo 2019)
4 m | 6.9 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 5.6616 | 5.377 | 5.0378 | 4.261 | 3.4426
| 25.8 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 7.8491 | 5.6686 | 5.3712 | 5.0528 | 4.6719
| 49.0 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 8.2241 | 5.6686 | 5.3712 | 5.0528 | 4.6719
| 57.6 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 8.2241 | 5.6686 | 5.3712 | 5.0528 | 4.6719
| 159.0 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 9.224 | 6.1687 | 5.3712 | 5.0528 | 4.6719
5 m | 6.9 kW | H |  | 0.35 |  | 0.65 | 0.8
|  | Lb |  | 6.2182 |  | 4.7498 | 4.7391
| 25.8 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 7.2555 | 6.9483 | 5.8426 | 4.7498 | 4.7391
| 49.0 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 8.6766 | 6.5311 | 5.8035 | 4.7498 | 4.7391
| 57.6 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 9.0678 | 6.5311 | 6.2207 | 5.141 | 4.7391
| 159.0 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 9.0678 | 6.5311 | 6.2207 | 5.141 | 4.7391
6 m | 6.9 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 8.7617 | 6.3452 | 5.9418 | 5.932 | 5.5182
| 25.8 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 9 | 8.0447 | 7.2267 | 5.932 | 6.3265
| 49.0 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 9.259 | 8.3556 | 7.2371 | 6.3258 | 6.3265
| 57.6 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 9.259 | 8.3556 | 7.2371 | 6.3258 | 6.3265
| 159.0 kW | H | 0 | 0.35 | 0.5 | 0.65 | 0.8
|  | Lb | 9.6632 | 8.3556 | 7.6412 | 6.8336 | 6.3265
Lb - Smoke back-layering length with Q - Heat relaease rate. (Guo 2019)
4 m | 0 m | Q | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Lb | 5.6616 | 7.8491 | 8.2241 | 8.2241 | 9.224
| 0.35 m | Q | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Lb | 5.377 | 5.6686 | 5.6686 | 5.6686 | 6.1687
| 0.50 m | Q | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 5.0378 | 5.3712 | 5.3712 | 5.66 | 5.3712
| 0.65 m | Lb | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 4.261 | 5.0528 | 5.0528 | 5.0528 | 5.0528
| 0.80 m | Lb | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 3.4426 | 4.6719 | 4.6719 | 4.6719 | 4.6719
5 m | 0 m | Q |  | 25.8 | 49 | 57.6 | 159
|  | Lb |  | 7.2555 | 8.6766 | 9.0678 | 9.0678
| 0.35 m | Q | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Lb | 6.2182 | 6.9483 | 6.5311 | 6.5311 | 6.5311
| 0.50 m | Q |  | 25.8 | 49 | 57.6 | 159
|  | Q |  | 5.8426 | 5.8035 | 6.2207 | 6.2207
| 0.65 m | Lb | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 4.7498 | 4.7498 | 4.7498 | 5.141 | 5.141
| 0.80 m | Lb | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 4.7391 | 4.7391 | 4.7391 | 4.7391 | 4.7391
6 m | 0 m | Q | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Lb | 8.7617 | 9 | 9.259 | 9.259 | 9.6632
| 0.35 m | Q | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Lb | 6.3452 | 8.0447 | 8.3556 | 8.3556 | 8.3556
| 0.50 m | Q | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 5.9418 | 7.2267 | 7.2371 | 7.2371 | 7.6412
| 0.65 m | Lb | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 5.932 | 5.932 | 6.3258 | 6.3258 | 6.8336
| 0.80 m | Lb | 6.9 | 25.8 | 49 | 57.6 | 159
|  | Q | 5.5182 | 6.3265 | 6.3265 | 6.3265 | 6.3265
Lb - Smoke back-layering length with D - Fire-shaft distance (Guo 2019)
0.35 m | 6.9 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.3547 | 6.2434 | 6.3617
| 25.8 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.6874 | 6.9352 | 8.0342
| 49.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.6785 | 6.5324 | 8.3494
| 57.6 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.6436 | 6.5149 | 8.358
| 159.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 6.1515 | 6.5149 | 8.3319
0.5 m | 6.9 kW | D | 1.5 | 2.5
|  | Lb | 5.0912 | 5.9449
| 25.8 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.3846 | 5.8426 | 7.2521
| 49.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.3846 | 5.8426 | 7.2521
| 57.6 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.3846 | 6.2161 | 7.2165
| 159.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.3313 | 6.2161 | 7.6256
0.65 m | 6.9 kW | D | 1.5 | 2 | 2.5
|  | Lb | 4.258 | 4.7424 | 5.9577
| 25.8 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.0683 | 4.7248 | 5.9577
| 49.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.0683 | 4.7248 | 6.3716
| 57.6 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.3501 | 5.1211 | 6.3364
| 159.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 5.0506 | 5.1123 | 6.8559
0.8 m | 6.9 kW | D | 1.5 | 2 | 2.5
|  | Lb | 3.4586 | 4.7267 | 5.5575
| 25.8 kW | D | 1.5 | 2 | 2.5
|  | Lb | 4.5779 | 4.7005 | 6.3096
| 49.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 4.5868 | 4.7005 | 6.3271
| 57.6 kW | D | 1.5 | 2 | 2.5
|  | Lb | 4.6218 | 4.7355 | 6.2833
| 159.0 kW | D | 1.5 | 2 | 2.5
|  | Lb | 4.613 | 4.7092 | 6.3271
Lb - Smoke back-layering length with V - ventilation velocity based on different ceiling extraction velocity (Tang 2016)
30 kW | 0.5 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 18.08 | 10.725 | 1.4625 | 1.421 | 1.4314
| 1.0 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 16.11 | 8.3 | 1.4625 | 1.421 | 1.4314
| 1.5 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 12.2 | 6.825 | 1.4625 | 1.421 | 1.4314
| 2.0 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 8.28 | 5.36 | 1.4625 | 1.421 | 1.4314
| 2.2 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 3.4 | 2.422 | 1.4625 | 1.421 | 1.4314
40 kW | 0.5 m/s | V |  | 0.5 | 0.8 | 1 | 1.2
|  | Lb |  | 12.48 | 2.51 | 1.03 | 1.03
| 1.0 m/s | V | 0.2997 | 0.4993 | 1.0007 | 1.2003 | 0.8011
|  | Lb | 16.5078 | 5.0165 | 1.0033 | 1.0033 | 1.7894
| 1.5 m/s | V | 0.2993 | 0.5005 | 0.801 | 1.0007 | 1.2014
|  | Lb | 13.0221 | 3.9821 | 1.9962 | 1.0033 | 0.9826
| 2.0 m/s | V | 0.2995 | 0.5016 | 0.8011 | 1.0007 | 1.2014
|  | Lb | 9.0296 | 3.0099 | 1.5411 | 1.0033 | 0.9826
| 2.2 m/s | V | 0.2998 | 0.5005 | 0.8011 | 1.0007 | 1.2014
|  | Lb | 3.5063 | 1.9962 | 0.9826 | 1.0033 | 0.9826
50 kW | 0.5 m/s | V |  | 0.5 | 0.8 | 1 | 1.2
|  | Lb |  | 14.0127 | 4.47 | 1.9968 | 0.9925
| 1.0 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 17.514 | 3.4838 | 0.9687 | 0.9925 | 9.9841
| 1.5 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 16.0242 | 3.0012 | 0.9687 | 0.9925 | 5.4309
| 2.0 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 13.5063 | 2.5186 | 0.9687 | 0.9925 | 4.0461
| 2.2 m/s | V | 0.3 | 0.5 | 0.8 | 1 | 1.2
|  | Lb | 7.0018 | 1.994 | 0.9687 | 0.9925 | 3.4796
Lb - Smoke back-layering length with V - ventilation velocity based on different ceiling extraction (Tang 2016)
40 kW | upstream | V | 0.2988 | 0.4999 | 0.7995 | 1.0006 | 1.2003
|  | Lb | 4.0018 | 3.5039 | 2.9977 | 2.0024 | 1.9979
| downstream | V | 0.3003 | 0.4999 | 0.8009 | 1.0006 | 1.2003
|  | Lb | 3.5123 | 2.9986 | 0.9925 | 0.9998 | 0.9992
50 kW | upstream | V | 0.301 | 0.5016 | 0.802 | 1.0012 | 1.2019
|  | Lb | 5.5067 | 4.5055 | 4.0004 | 4.0077 | 3.5029
| downstream | V | 0.301 | 0.5015 | 0.8016 | 1.0009 | 1.2016
|  | Lb | 5.0103 | 3.5048 | 1.999 | 0.9978 | 0.9973

## Database
Scale factor | L [m] | W [m] | H [m] | Fire source | Fire area | Q [kW] | Shaft interval [m] | Shaft height [m] | fire shaft distance | Lb [m] | Lb* | V [m/s] | V* | Ref | Remarks
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 135.3 | - | - | - | 0.15 | - | 0.54 | - | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 151.8 | - | - | - | 0 | - | 0.87 | - | [2] |  | Calculation ways for flame length
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 254.7 | - | - | - | 0.205 | - | 0.45 | - | [2] |  | L | Tunnel length
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 320.8 | - | - | - | NA | - | 0.46 | - | [2] |  | W | Tunnel width
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 145.8 | - | - | - | 0.205 | - | 0.56 | - | [2] |  | H | Tunnel height
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 117.9 | - | - | - | 0.7 | - | 0.45 | - | [2] |  | Q | Heat release rate
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 141.3 | - | - | - | 2.2 | - | 0.38 | - | [2] |  | Lb | Backing up distance
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 142.8 | - | - | - | NA | - | 0.54 | - | [2] |  | V | Ventilation velocity
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | 305.2 | - | - | - | NA | - | 0.76 | - | [2]
1:23 | 10 | 0.4 | 0.3 | wood cribs | - | 103.7 | - | - | - | 0 | - | 0.54 | - | [2]
1:23 | 10 | 0.4 | 0.3 | wood cribs | - | 106.7 | - | - | - | 0 | - | 0.86 | - | [2]
1:23 | 10 | 0.4 | 0.3 | wood cribs | - | 102.2 | - | - | - | 1.04 | - | 0.33 | - | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | - | - | - | - | - | 7.5875 | - | 0.2741 | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | - | - | - | - | - | 2.7429 | - | 0.3209 | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | - | - | - | - | - | 1.152 | - | 0.3195 | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | - | - | - | - | - | 1.1519 | - | 0.3264 | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | - | - | - | - | - | 0.9662 | - | 0.3852 | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | - | - | - | - | - | 1.1505 | - | 0.4025 | [2]
1:23 | 10 | 0.4 | 0.2 | wood cribs | - | - | - | - | - | - | 0.4791 | - | 0.6183 | [2]
1:23 | 10 | 0.4 | 0.3 | wood cribs | - | - | - | - | - | - | 5.5274 | - | 0.2926 | [2]
1:23 | 10 | 0.4 | 0.3 | wood cribs | - | - | - | - | - | - | 0.4817 | - | 0.4712 | [2]
1:23 | 10 | 0.4 | 0.3 | wood cribs | - | - | - | - | - | - | 0.4767 | - | 0.7502 | [2]
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 0.2503 | - | 0.4646 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 0.3498 | - | 0.4453 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 0.4493 | - | 0.4291 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 0.6 | - | 0.4123 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 0.7999 | - | 0.3953 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 0.1502 | - | 0.5474 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 0.2993 | - | 0.5255 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 0.4502 | - | 0.5022 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 0.65 | - | 0.475 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 0.8001 | - | 0.4504 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 0.2 | - | 0.5844 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 0.3998 | - | 0.5444 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 0.6501 | - | 0.519 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 0.8002 | - | 0.5001 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 0.2498 | - | 0.6206 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 0.3501 | - | 0.6038 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 0.5499 | - | 0.5718 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 0.6999 | - | 0.5512 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 0.8002 | - | 0.5393 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 9.2 | - | - | - | 0.2503 | - | 0.6334 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 9.2 | - | - | - | 0.4003 | - | 0.6118 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 9.2 | - | - | - | 0.7 | - | 0.5644 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 12.7 | - | - | - | 0.3514 | - | 0.6179 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 12.7 | - | - | - | 0.6505 | - | 0.5678 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 12.7 | - | - | - | 0.85 | - | 0.5451 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 0.3 | - | 0.6221 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 0.5503 | - | 0.5864 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 0.7004 | - | 0.5646 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 0.9005 | - | 0.54 | - | [3]
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 0.9973 | - | - | 0.9281 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 1.3978 | - | - | 0.8908 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 1.7982 | - | - | 0.8582 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 1.8 | - | - | - | 2.4016 | - | - | 0.8256 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 0.597 | - | - | 0.9615 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 1.7982 | - | - | 0.8818 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 1.1948 | - | - | 0.922 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 2.596 | - | - | 0.834 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 3.2 | - | - | - | 3.1995 | - | - | 0.79 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 0.7973 | - | - | 0.928 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 1.5981 | - | - | 0.865 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 2.5989 | - | - | 0.8241 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 4.8 | - | - | - | 3.1995 | - | - | 0.7938 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 0.9973 | - | - | 0.9334 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 1.395 | - | - | 0.9076 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 2.1957 | - | - | 0.8606 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 2.7991 | - | - | 0.8295 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 6.7 | - | - | - | 3.1994 | - | - | 0.8113 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 9.2 | - | - | - | 0.9973 | - | - | 0.9456 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 9.2 | - | - | - | 1.5979 | - | - | 0.9137 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 9.2 | - | - | - | 2.5989 | - | - | 0.8363 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 9.2 | - | - | - | 2.799 | - | - | 0.8409 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 12.7 | - | - | - | 0.1966 | - | - | 0.9919 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 12.7 | - | - | - | 1.3977 | - | - | 0.9228 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 12.7 | - | - | - | 2.596 | - | - | 0.8484 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 12.7 | - | - | - | 3.3967 | - | - | 0.8143 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 0 | - | - | 1.0002 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 1.1976 | - | - | 0.9289 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 2.1985 | - | - | 0.8765 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 2.799 | - | - | 0.8447 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 3.5997 | - | - | 0.8068 | [3] | Dimensionless confinement velocity
- | 12 | 0.25 | 0.25 | Propane | - | 16.5 | - | - | - | 2.5989 | - | - | 0.834 | [3] | Dimensionless confinement velocity
1:20 | 10 | 0.3 | 0.25 | Heptane | 0.08 | 185.3 | - | - | - | 0–0.25 | - | 0.67 | - | [4]
1:20 | 10 | 0.45 | 0.25 | Heptane | 0.11 | 172.2 | - | - | - | 0–0.25 | - | 0.67 | - | [4]
1:20 | 10 | 0.6 | 0.25 | Heptane | 0.15 | 214.8 | - | - | - | 0.5–0.75 | - | 0.67 | - | [4]
1:20 | 10 | 0.3 | 0.4 | Heptane | 0.12 | 155.8 | - | - | - | 0.5–0.75 | - | 0.67 | - | [4]
1:20 | 10 | 0.45 | 0.4 | Heptane | 0.18 | 139.4 | - | - | - | 2.5–2.75 | - | 0.67 | - | [4]
1:20 | 10 | 0.6 | 0.4 | Heptane | 0.24 | 162.4 | - | - | - | >3.75 | - | 0.5 | - | [4]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 4 | 0 | - | 5.6616 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 4 | 0.35 | - | 5.377 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 4 | 0.5 | - | 5.0378 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 4 | 0.65 | - | 4.261 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 4 | 0.8 | - | 3.4426 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 4 | 0 | - | 7.8491 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 4 | 0.35 | - | 5.6686 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 4 | 0.5 | - | 5.3712 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 4 | 0.65 | - | 5.0528 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 4 | 0.8 | - | 4.6719 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 4 | 0 | - | 8.2241 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 4 | 0.35 | - | 5.6686 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 4 | 0.5 | - | 5.3712 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 4 | 0.65 | - | 5.0528 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 4 | 0.8 | - | 4.6719 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 4 | 0 | - | 8.2241 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 4 | 0.35 | - | 5.6686 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 4 | 0.5 | - | 5.3712 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 4 | 0.65 | - | 5.0528 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 4 | 0.8 | - | 4.6719 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 4 | 0 | - | 9.224 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 4 | 0.35 | - | 6.1687 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 4 | 0.5 | - | 5.3712 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 4 | 0.65 | - | 5.0528 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 4 | 0.8 | - | 4.6719 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 5 | 0.35 | - | 6.2182 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 5 | 0.65 | - | 4.7498 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 5 | 0.8 | - | 4.7391 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 5 | 0 | - | 7.2555 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 5 | 0.35 | - | 6.9483 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 5 | 0.5 | - | 5.8426 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 5 | 0.65 | - | 4.7498 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 5 | 0.8 | - | 4.7391 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 5 | 0 | - | 8.6766 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 5 | 0.35 | - | 6.5311 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 5 | 0.5 | - | 5.8035 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 5 | 0.65 | - | 4.7498 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 5 | 0.8 | - | 4.7391 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 5 | 0 | - | 9.0678 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 5 | 0.35 | - | 6.5311 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 5 | 0.5 | - | 6.2207 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 5 | 0.65 | - | 5.141 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 5 | 0.8 | - | 4.7391 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 5 | 0 | - | 9.0678 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 5 | 0.35 | - | 6.5311 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 5 | 0.5 | - | 6.2207 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 5 | 0.65 | - | 5.141 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 5 | 0.8 | - | 4.7391 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 6 | 0 | - | 8.7617 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 6 | 0.35 | - | 6.3452 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 6 | 0.5 | - | 5.9418 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 6 | 0.65 | - | 5.932 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | 6 | 0.8 | - | 5.5182 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 6 | 0 | - | 9 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 6 | 0.35 | - | 8.0447 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 6 | 0.5 | - | 7.2267 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 6 | 0.65 | - | 5.932 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | 6 | 0.8 | - | 6.3265 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 6 | 0 | - | 9.259 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 6 | 0.35 | - | 8.3556 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 6 | 0.5 | - | 7.2371 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 6 | 0.65 | - | 6.3258 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | 6 | 0.8 | - | 6.3265 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 6 | 0 | - | 9.259 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 6 | 0.35 | - | 8.3556 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 6 | 0.5 | - | 7.2371 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 6 | 0.65 | - | 6.3258 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | 6 | 0.8 | - | 6.3265 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 6 | 0 | - | 9.6632 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 6 | 0.35 | - | 8.3556 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 6 | 0.5 | - | 7.6412 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 6 | 0.65 | - | 6.8336 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | 6 | 0.8 | - | 6.3265 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.35 | 1.5 | 5.3547 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.35 | 2 | 6.2434 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.35 | 2.5 | 6.3617 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.35 | 1.5 | 5.6874 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.35 | 2 | 6.9352 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.35 | 2.5 | 8.0342 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.35 | 1.5 | 5.6785 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.35 | 2 | 6.5324 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.35 | 2.5 | 8.3494 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.35 | 1.5 | 5.6436 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.35 | 2 | 6.5149 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.35 | 2.5 | 8.358 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.35 | 1.5 | 6.1515 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.35 | 2 | 6.5149 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.35 | 2.5 | 8.3319 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.5 | 1.5 | 5.0912 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.5 | 2.5 | 5.9449 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.5 | 1.5 | 5.3846 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.5 | 2 | 5.8426 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.5 | 2.5 | 7.2521 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.5 | 1.5 | 5.3846 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.5 | 2 | 5.8426 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.5 | 2.5 | 7.2521 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.5 | 1.5 | 5.3846 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.5 | 2 | 6.2161 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.5 | 2.5 | 7.2165 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.5 | 1.5 | 5.3313 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.5 | 2 | 6.2161 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.5 | 2.5 | 7.6256 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.65 | 1.5 | 4.258 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.65 | 2 | 4.7424 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.65 | 2.5 | 5.9577 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.65 | 1.5 | 5.0683 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.65 | 2 | 4.7248 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.65 | 2.5 | 5.9577 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.65 | 1.5 | 5.0683 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.65 | 2 | 4.7248 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.65 | 2.5 | 6.3716 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.65 | 1.5 | 5.3501 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.65 | 2 | 5.1211 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.65 | 2.5 | 6.3364 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.65 | 1.5 | 5.0506 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.65 | 2 | 5.1123 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.65 | 2.5 | 6.8559 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.8 | 1.5 | 3.4586 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.8 | 2 | 4.7267 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 6.9 | - | 0.8 | 2.5 | 5.5575 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.8 | 1.5 | 4.5779 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.8 | 2 | 4.7005 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 25.8 | - | 0.8 | 2.5 | 6.3096 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.8 | 1.5 | 4.5868 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.8 | 2 | 4.7005 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 49 | - | 0.8 | 2.5 | 6.3271 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.8 | 1.5 | 4.6218 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.8 | 2 | 4.7355 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 57.6 | - | 0.8 | 2.5 | 6.2833 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.8 | 1.5 | 4.613 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.8 | 2 | 4.7092 | - | - | - | [7]
1:10 | 20.8 | 1.2 | 0.5 | Heptane | - | 159 | - | 0.8 | 2.5 | 6.3271 | - | - | - | [7]

## Reference lists
Ref. No. | Title
1 | Parametrical study of the back flow occurrence in case of a buoyant release into a rectangular channel. (Vauquelin 2005)
2 | Model scale tunnel fire tests with longitudinal ventilation.(Ingason 2010)
3 | Study of critical velocity and backlayering length in longitudinally ventilated tunnel fires.(Li 2010)
4 | Effect of tunnel cross section on gas temperatures and heat fluxes in case of large heat release rate.(Fan 2016)
5 | A model for predicting smoke back-layering length in tunnel fi res with the combination of longitudinal ventilation and point extraction ventilation in the roof.(Wang 2018)
6 | Effects of ambient pressure on smoke back-layering in subway tunnel fires. (Wu 2018)
7 | Experimental studies on the gas temperature and smoke back-layering length of fi res in a shallow urban road tunnel with large cross-sectional vertical shafts.(Guo 2019)
8 | Thermal smoke back-layering flow length with ceiling extraction at upstream side of fire source in a longitudinal ventilated tunnel.(Tang 2016)