## 3.7 Plug-holing
Occurrence of plug-holing with Q - Heat release rate and H - shaft height (2012 Ji)
HRR (kW) | Shaft height
| 0.2 m | 0.4 m | 0.6 m | 0.8 m | 1.0 m
6.95 | No | Yes | Yes | Yes | Yes
12.56 | No | Yes | Yes | Yes | Yes
20.21 | No | Yes | Yes | Yes | Yes
29.57 | No | Yes | Yes | Yes | Yes
36.66 | No | No | Yes | Yes | Yes
44.01 | No | No | Yes | Yes | Yes
53.37 | No | No | Yes | Yes | Yes
No: nonoccurrence of plug-holing.
Yes: occurrence of plug-holing.
Plug-holing and values of Ri' under different experiments (2012 Ji)
6.95 kW | H | 0.1999 | 0.4002 | 0.6006 | 0.8003 | 1
| Ri' | 1.2498 | 2.4974 | 3.7395 | 4.9815 | 6.2292
12.56 kW | H | 0.1999 | 0.4002 | 0.6006 | 0.8003 | 1
| Ri' | 1.1883 | 2.3801 | 3.5718 | 4.7635 | 5.9553
20.21 kW | H | 0.1999 | 0.3996 | 0.5998 | 0.8002 | 0.9999
| Ri' | 0.7803 | 1.5529 | 2.3254 | 3.098 | 3.8761
29.57 kW | H | 0.1999 | 0.4002 | 0.5998 | 0.8002 | 0.9999
| Ri' | 0.7244 | 1.4578 | 2.1913 | 2.9191 | 3.6469
36.66 kW | H | 0.1992 | 0.4008 | 0.5992 | 0.8002 | 0.9999
| Ri' | 0.6573 | 1.3181 | 1.9733 | 2.6397 | 3.2948
44.01 kW | H | 0.1999 | 0.4014 | 0.6005 | 0.8008 | 1.0005
| Ri' | 0.6461 | 1.2902 | 1.9342 | 2.5894 | 3.2278
53.37 kW | H | 0.1999 | 0.3995 | 0.5992 | 0.7995 | 0.9998
| Ri' | 0.5791 | 1.156 | 1.7274 | 2.3099 | 2.8812
Criterion of new modified Froude number for the occurrence of plug-holing (2017 Beak)
AR = 1 | Q | 1.1923 | 3.1907 | 4.4943 | 10.1057
| FrN | 4.2416 | 3.1732 | 3.1127 | 2.9205
AR = 0.83 | Q | 1.1928 | 3.1911 | 4.4947 | 10.0956
| FrN | 4.0109 | 2.9919 | 2.9506 | 2.8738
AR = 0.71 | Q | 1.1935 | 3.1913 | 4.4948 | 10.0959
| FrN | 3.7225 | 2.904 | 2.8738 | 2.7529
AR = 0.63 | Q | 1.1942 | 3.1966 | 4.5002 | 10.1013
| FrN | 3.4094 | 2.7995 | 2.7378 | 2.6499
AR = 0.56 | Q | 1.1998 | 3.202 | 4.4954 | 10.0963
| FrN | 3.2006 | 2.687 | 2.6307 | 2.6019
Occurrence of plug-holing with Q - Heat release rate and smoke exhaust rate (2018 Jiang)
Smoke exhaust rate (m3/s) | Heat release rate
| 2.8 kW | 5.6 kW | 11.2 kW | 16.8 kW
0 | NO | NO | NO | NO
0.006 | NO | NO | NO | NO
0.011 | NO | NO | NO | NO
0.017 | ∼ | NO | NO | NO
0.022 | ∼ | NO | NO | NO
0.028 | ∼ | ∼ | NO | NO
0.034 | YES | ∼ | NO | NO
0.039 | YES | ∼ | NO | NO
0.045 | YES | YES | ∼ | ∼
0.05 | YES | YES | ∼ | ∼
0.056 | YES | YES | ∼ | ∼
0.061 | — | YES | ∼ | ∼
0.067 | — | YES | ∼ | ∼
0.073 | — | — | YES | ∼
0.078 | — | — | YES | YES
0.084 | — | — | YES | YES
0.089 | — | — | YES | YES
0.095 | — | — | — | YES
0.101 | — | — | — | YES
“NO”: Non-occurrence of plug-holing YES: Occurrence of plug-holing “∼”: Transitional region “—”: No tests.
Plug-holing and values of Fr - Froude number under different experiments (2018 Jiang)
exhaust vents: 20cm × 7.5cm
[16 empty] | vent spacing: 3 m |  | vent number: 2
2.8 kW | R | 0 | 0.006 | 0.011 | 0.017 | 0.022 | 0.028 | 0.034 | 0.039 | 0.045 | 0.05 | 0.056
| Fr | 0.1531 | 0.4336 | 0.7532 | 1.1403 | 1.4208 | 1.7972 | 2.1417 | 2.4435 | 2.8129 | 3.1112 | 3.4521
5.6 Kw | R | 0 | 0.006 | 0.011 | 0.017 | 0.022 | 0.028 | 0.034 | 0.039 | 0.045 | 0.05 | 0.056 | 0.061 | 0.067
| Fr | 0.114 | 0.3164 | 0.5295 | 0.6928 | 0.9308 | 1.1509 | 1.3888 | 1.5735 | 1.8043 | 1.9783 | 2.2021 | 2.4045 | 2.6104
11.2 kW | R | 0 | 0.006 | 0.011 | 0.017 | 0.022 | 0.028 | 0.034 | 0.039 | 0.045 | 0.05 | 0.056 | 0.061 | 0.067 | 0.073 | 0.078 | 0.084 | 0.089
| Fr | 0.0856 | 0.2205 | 0.3448 | 0.5011 | 0.6076 | 0.7816 | 0.9059 | 1.0231 | 1.1296 | 1.2788 | 1.4137 | 1.5309 | 1.6587 | 1.7511 | 1.8896 | 2.021 | 2.1594
16.8 kW | R | 0 | 0.006 | 0.011 | 0.017 | 0.022 | 0.028 | 0.034 | 0.039 | 0.045 | 0.05 | 0.056 | 0.061 | 0.067 | 0.073 | 0.078 | 0.084 | 0.089 | 0.095 | 0.101
| Fr | 0.0998 | 0.2063 | 0.3519 | 0.4656 | 0.5756 | 0.7638 | 0.8775 | 0.9876 | 1.1118 | 1.2219 | 1.3569 | 1.4634 | 1.5771 | 1.6658 | 1.783 | 1.9038 | 1.9996 | 2.1665 | 2.2376
R - Smoke exhaust rate (m/s)

## Database_Plug-holing
Scale factor | L [m] | W [m] | H [m] | Fuel | Fire location(from opening /m) | Shaft size | shaft location (from fire/m) | Shaft height [m] | AR | Q [kW] | V [m3] | plug-holing | Ri' | FrN | Ref | Remarks
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.2 | - | 6.95 | - | N | 1.2498 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.2 | - | 12.56 | - | N | 1.1883 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.2 | - | 20.21 | - | N | 0.7803 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.2 | - | 29.57 | - | N | 0.7244 | - | [1] |  | AR | aspect ratios
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.2 | - | 36.66 | - | N | 0.6573 | - | [1] |  | V | Smoke exhaust rate (m3/s)
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.2 | - | 44.01 | - | N | 0.6461 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.2 | - | 53.37 | - | N | 0.5791 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.4 | - | 6.95 | - | Y | 2.4974 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.4 | - | 12.56 | - | Y | 2.3801 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.4 | - | 20.21 | - | Y | 1.5529 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.4 | - | 29.57 | - | Y | 1.4578 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.4 | - | 36.66 | - | N | 1.3181 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.4 | - | 44.01 | - | N | 1.2902 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.4 | - | 53.37 | - | N | 1.156 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.6 | - | 6.95 | - | Y | 3.7395 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.6 | - | 12.56 | - | Y | 3.5718 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.6 | - | 20.21 | - | Y | 2.3254 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.6 | - | 29.57 | - | Y | 2.1913 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.6 | - | 36.66 | - | Y | 1.9733 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.6 | - | 44.01 | - | Y | 1.9342 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.6 | - | 53.37 | - | Y | 1.7274 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.8 | - | 6.95 | - | Y | 4.9815 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.8 | - | 12.56 | - | Y | 4.7635 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.8 | - | 20.21 | - | Y | 3.098 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.8 | - | 29.57 | - | Y | 2.9191 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.8 | - | 36.66 | - | Y | 2.6397 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.8 | - | 44.01 | - | Y | 2.5894 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 0.8 | - | 53.37 | - | Y | 2.3099 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 1 | - | 6.95 | - | Y | 6.2292 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 1 | - | 12.56 | - | Y | 5.9553 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 1 | - | 20.21 | - | Y | 3.8761 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 1 | - | 29.57 | - | Y | 3.6469 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 1 | - | 36.66 | - | Y | 3.2948 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 1 | - | 44.01 | - | Y | 3.2278 | - | [1]
0.16667 | 6 | 2 | 0.9 | methanol | 1.2 | 0.3m × 0.3m | 3 | 1 | - | 53.37 | - | Y | 2.8812 | - | [1]
1:20 | 7 | 0.3 | 0.3 | n-Heptane | 2.9 | 0.1m × 0.12m | 2.3 | 0.15 | 1 | 1.1923 | - | N | - | 4.2416 | [2]
1:20 | 7 | 0.3 | 0.3 | n-Heptane | 2.9 | 0.1m × 0.12m | 2.3 | 0.15 | 1 | 3.1907 | - | N | - | 3.1732 | [2]
1:20 | 7 | 0.3 | 0.3 | n-Heptane | 2.9 | 0.1m × 0.12m | 2.3 | 0.15 | 1 | 4.4943 | - | N | - | 3.1127 | [2]
1:20 | 7 | 0.3 | 0.3 | n-Heptane | 2.9 | 0.1m × 0.12m | 2.3 | 0.15 | 1 | 10.1057 | - | N | - | 2.9205 | [2]
1:20 | 7 | 0.36 | 0.3 | n-Heptane | 2.9 | 0.12m × 0.12m | 2.3 | 0.15 | 0.83 | 1.1928 | - | N | - | 4.0109 | [2]
1:20 | 7 | 0.36 | 0.3 | n-Heptane | 2.9 | 0.12m × 0.12m | 2.3 | 0.15 | 0.83 | 3.1911 | - | N | - | 2.9919 | [2]
1:20 | 7 | 0.36 | 0.3 | n-Heptane | 2.9 | 0.12m × 0.12m | 2.3 | 0.15 | 0.83 | 4.4947 | - | N | - | 2.9506 | [2]
1:20 | 7 | 0.36 | 0.3 | n-Heptane | 2.9 | 0.12m × 0.12m | 2.3 | 0.15 | 0.83 | 10.0956 | - | N | - | 2.8738 | [2]
1:20 | 7 | 0.42 | 0.3 | n-Heptane | 2.9 | 0.14m × 0.12m | 2.3 | 0.15 | 0.71 | 1.1935 | - | N | - | 3.7225 | [2]
1:20 | 7 | 0.42 | 0.3 | n-Heptane | 2.9 | 0.14m × 0.12m | 2.3 | 0.15 | 0.71 | 3.1913 | - | N | - | 2.904 | [2]
1:20 | 7 | 0.42 | 0.3 | n-Heptane | 2.9 | 0.14m × 0.12m | 2.3 | 0.15 | 0.71 | 4.4948 | - | N | - | 2.8738 | [2]
1:20 | 7 | 0.42 | 0.3 | n-Heptane | 2.9 | 0.14m × 0.12m | 2.3 | 0.15 | 0.71 | 10.0959 | - | N | - | 2.7529 | [2]
1:20 | 7 | 0.48 | 0.3 | n-Heptane | 2.9 | 0.16m × 0.12m | 2.3 | 0.15 | 0.63 | 1.1942 | - | N | - | 3.4094 | [2]
1:20 | 7 | 0.48 | 0.3 | n-Heptane | 2.9 | 0.16m × 0.12m | 2.3 | 0.15 | 0.63 | 3.1966 | - | N | - | 2.7995 | [2]
1:20 | 7 | 0.48 | 0.3 | n-Heptane | 2.9 | 0.16m × 0.12m | 2.3 | 0.15 | 0.63 | 4.5002 | - | Y | - | 2.7378 | [2]
1:20 | 7 | 0.48 | 0.3 | n-Heptane | 2.9 | 0.16m × 0.12m | 2.3 | 0.15 | 0.63 | 10.1013 | - | Y | - | 2.6499 | [2]
1:20 | 7 | 0.54 | 0.3 | n-Heptane | 2.9 | 0.18m × 0.12m | 2.3 | 0.15 | 0.56 | 1.1998 | - | N | - | 3.2006 | [2]
1:20 | 7 | 0.54 | 0.3 | n-Heptane | 2.9 | 0.18m × 0.12m | 2.3 | 0.15 | 0.56 | 3.202 | - | Y | - | 2.687 | [2]
1:20 | 7 | 0.54 | 0.3 | n-Heptane | 2.9 | 0.18m × 0.12m | 2.3 | 0.15 | 0.56 | 4.4954 | - | Y | - | 2.6307 | [2]
1:20 | 7 | 0.54 | 0.3 | n-Heptane | 2.9 | 0.18m × 0.12m | 2.3 | 0.15 | 0.56 | 10.0963 | - | Y | - | 2.6019 | [2]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0 | N | - | 0.1531 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.006 | N | - | 0.4336 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.011 | N | - | 0.7532 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.017 | - | - | 1.1403 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.022 | - | - | 1.4208 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.028 | - | - | 1.7972 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.034 | Y | - | 2.1417 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.039 | Y | - | 2.4435 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.045 | Y | - | 2.8129 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.05 | Y | - | 3.1112 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 2.8 | 0.056 | Y | - | 3.4521 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0 | N | - | 0.114 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.006 | N | - | 0.3164 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.011 | N | - | 0.5295 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.017 | N | - | 0.6928 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.022 | N | - | 0.9308 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.028 | - | - | 1.1509 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.034 | - | - | 1.3888 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.039 | - | - | 1.5735 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.045 | Y | - | 1.8043 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.05 | Y | - | 1.9783 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.056 | Y | - | 2.2021 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.061 | Y | - | 2.4045 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 5.6 | 0.067 | Y | - | 2.6104 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0 | N | - | 0.0856 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.006 | N | - | 0.2205 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.011 | N | - | 0.3448 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.017 | N | - | 0.5011 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.022 | N | - | 0.6076 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.028 | N | - | 0.7816 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.034 | N | - | 0.9059 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.039 | N | - | 1.0231 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.045 | - | - | 1.1296 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.05 | - | - | 1.2788 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.056 | - | - | 1.4137 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.061 | - | - | 1.5309 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.067 | - | - | 1.6587 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.073 | Y | - | 1.7511 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.078 | Y | - | 1.8896 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.084 | Y | - | 2.021 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 11.2 | 0.089 | Y | - | 2.1594 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0 | N | - | 0.0998 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.006 | N | - | 0.2063 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.011 | N | - | 0.3519 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.017 | N | - | 0.4656 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.022 | N | - | 0.5756 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.028 | N | - | 0.7638 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.034 | N | - | 0.8775 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.039 | N | - | 0.9876 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.045 | - | - | 1.1118 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.05 | - | - | 1.2219 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.056 | - | - | 1.3569 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.061 | - | - | 1.4634 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.067 | - | - | 1.5771 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.073 | - | - | 1.6658 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.078 | Y | - | 1.783 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.084 | Y | - | 1.9038 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.089 | Y | - | 1.9996 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.095 | Y | - | 2.1665 | [4]
1:20 | 22 | 0.6 | 0.27 | methanol | 11 | 20 cm × 7.5 cm | - | - | - | 16.8 | 0.101 | Y | - | 2.2376 | [4]

## Reference lists
Ref. No | Title
1 | A study of the effect of plug-holing and boundary layer separation on natural ventilation with vertical shaft in urban road tunnel fires. (Ji et al. 2012)
2 | Experimental study on the effect of heat release rate and aspect ratio of tunnel on the plug-holing phenomena in shallow underground tunnels. (Baek et al. 2017)
3 | Modeling for predicting the temperature distribution of smoke during a fire in an underground road tunnel with vertical shafts. (Takeuchi et al. 2017)
4 | An experimental study on plug-holing in tunnel fi re with central smoke extraction. (Jiang et al. 2018)